## Instructions
General Guidance
Green shaded cells require input data
Orange shaded cells are calculation outputs. These cells contain formulas and should not be modified.
The 'Calc Workings' tab should not be modified
Complete the following inputs
Air gap at the fault location. | The gap in millimeters between opposite polarity conductors/terminals at the arcing fault location. In general, an arc gap of 25mm should be used, unless the actual arc gap is available from the product literature, site data collection or other source of information.
Working distance | The distance in millimeters between the fault location and the person exposed to the hazard. In general a working distance of 455mm should be used.
Fault Location | Select the fault location from the drop down list: - Open Air - Panel/Enclosure: An Enclosure/Panel without a circuit breaker or isolating switch is defined as a ‘panel/enclosure’ - Switchboard: An Enclosure/Panel with a circuit breaker is defined as a ‘switchboard’.
String 1 - 5 | Input string data according to number of parallel battery strings. Strings cells not used can be left blank,'0', and rolled up/down as needed using the '+' / '-' tabs on the far left hand side.
- String Voltage | The total string voltage in volts (the sum of individual series connected battery module voltages)
- Battery Internal Resistance | Individual battery module internal resistance in ohms. This value is ideally obtained from the manufacturer's datasheet. Typical values can be used based on the battery type and voltage if specific manufacturer data is unavailable.
- Cable DC Resistance | The DC resistance of the cabling between the battery string terminals and the fault location in ohms. Large and/or short route length cables can be neglected, where the cable resistance is negligible in comparison to the sum of the battery internal resistances across a string.
- Number of Batteries per String | The number of individual batteries modules comprising the string.
String Protection Trip Times | The protection device clearing time in seconds for individual strings. This may need to be assessed using the protection device time current curve. The string arc fault current value is shown alongside the string trip time input cells, this information can be used to evaluate the trip time using the time-current curve of the protection device. Where the protection trip time exceeds 2s or there isn't a string protection device present, 2s should be used as the string trip time.
Calculation Outputs
String bolted fault current | The fault current contribution in amps for an individual string into a bolted fault location.
Bolted Fault Current | The total fault current in amps from all strings into a bolted fault location.
Arc Resistance | The DC resistance across the arc gap in ohms.
String Arc Fault Current | The fault current contribution in amps for an individual string into an arcing fault location.
Arc Fault Current | The total fault current in amps from all strings into an arcing fault location.
Arc Flash Incident Energy | The energy level a person is exposed to in cal/cm2 at the defined working distance.
Arc Flash Boundary | The distance from the fault location where the incident energy is equal to 1.2 cal/cm2

## DC Arc Flash
DC ARC FLASH CALCULATION SHEET
WATER CORPORATION | [6 empty] | PROJECT
JOB No.
SUBJECT: | [6 empty] | CALC REF. No.:
[7 empty] | SHEET |  | OF |  |  | REV: | 0
REF. DRG. NO.: |  | MADE BY: |  |  |  | CHECKED BY: |  |  |  | APPROVED BY:
ITEM: |  | DATE: |  |  |  | DATE: |  |  |  | DATE:
FILE: | C:\Users\willcoc0\AppData\Local\Microsoft\Windows\INetCache\Content.Outlook\0KF66ELP\DS 29 Addendum - DC Arc Flash - Ammerman Calculation Method.xlsx
Calculation Initial Input Data
Fault Location Air Gap (G) (mm) | [8 empty] | Typically 25mm
Working Distance (D) (mm) | [8 empty] | Typically 455mm
Fault Location
String 1
String Voltage (VDC) | [7 empty] | V | Design docs
Battery Internal Resistance (Rb) | [7 empty] | Ohms | Vendor data / design docs
Cable DC Resistance (Rc) | [7 empty] | Ohms | Vendor data / design docs
Number of Batteries per String (Nb) | [8 empty] | Design docs
Bolted Fault Current (Ib1) |  |  |  | - |  |  |  | Amps
String 2
Battery Voltage (VDC) (V) | [7 empty] | V | Vendor data / design docs
Battery Internal Resistance (Rb) (Ohms) | [7 empty] | Ohms | Vendor data / design docs
Cable DC Resistance (Rc) (Ohms) | [7 empty] | Ohms | Vendor data / design docs
Number of Batteries per String (Nb) | [8 empty] | Design docs
Bolted Fault Current (Ib1) |  |  |  | - |  |  |  | Amps
String 3
Battery Voltage (VDC) (V) | [7 empty] | V | Vendor data / design docs
Battery Internal Resistance (Rb) (Ohms) | [7 empty] | Ohms | Vendor data / design docs
Cable DC Resistance (Rc) (Ohms) | [7 empty] | Ohms | Vendor data / design docs
Number of Batteries per String (Nb) | [8 empty] | Design docs
Bolted Fault Current (Ib1) |  |  |  | - |  |  |  | Amps
String 4
Battery Voltage (VDC) (V) | [7 empty] | V | Vendor data / design docs
Battery Internal Resistance (Rb) (Ohms) | [7 empty] | Ohms | Vendor data / design docs
Cable DC Resistance (Rc) (Ohms) | [7 empty] | Ohms | Vendor data / design docs
Number of Batteries per String (Nb) | [8 empty] | Design docs
Bolted Fault Current (Ib1) |  |  |  | - |  |  |  | Amps
String 5
Battery Voltage (VDC) (V) | [7 empty] | V | Vendor data / design docs
Battery Internal Resistance (Rb) (Ohms) | [7 empty] | Ohms | Vendor data / design docs
Cable DC Resistance (Rc) (Ohms) | [7 empty] | Ohms | Vendor data / design docs
Number of Batteries per String (Nb) | [8 empty] | Design docs
Bolted Fault Current (Ib1) |  |  |  | - |  |  |  | Amps
Bolted Fault Current (Ib) |  |  |  | 0 |  |  |  | Amps
Source Resistance (Rsource) |  |  |  | - |  |  |  | Ohms
Arc Resistance (Rarc) & Arc Fault Current (Iarc)
Arc Resistance (Rarc) |  |  |  | - |  |  |  | Ohms
Arc Fault Current (Iarc) |  |  |  | - |  |  |  | Amps
Protection Trip Times
String 1 Protection Trip Time (t1) |  |  | s |  | String 1 Arc Fault Current |  |  |  | - |  | Amps
String 2 Protection Trip Time (t2) |  |  | s |  | String 2 Arc Fault Current |  |  |  | - |  | Amps
String 3 Protection Trip Time (t3) |  |  | s |  | String 3 Arc Fault Current |  |  |  | - |  | Amps
String 4 Protection Trip Time (t4) |  |  | s |  | String 4 Arc Fault Current |  |  |  | - |  | Amps
String 5 Protection Trip Time (t5) |  |  | s |  | String 5 Arc Fault Current |  |  |  | - |  | Amps
Arc Flash Incident Energy |  |  |  | - |  |  |  | Cal/cm2
Arc Flash Boundary |  |  |  | - |  |  |  | mm

## Calc Workings
DO NOT MODIFY THE CELLS ON THIS WORKSHEET
iteration | I arc | R arc | Fault Location |  |  | String Arc Fault Current
0 | 0 | #DIV/0! | Open Air |  |  | branch 1 | 0
1 | #DIV/0! | #DIV/0! | Panel/Enclosure |  |  | branch 2 | 0
2 | #DIV/0! | #DIV/0! | Switchboard |  |  | branch 3 | 0
3 | #DIV/0! | #DIV/0! |  |  |  | branch 4 | 0
4 | #DIV/0! | #DIV/0! |  |  |  | branch 5 | 0
5 | #DIV/0! | #DIV/0!
6 | #DIV/0! | #DIV/0! | Stepped Arc Fault Current | [5 empty] | arc current | trip time
7 | #DIV/0! | #DIV/0! | 1 | 0 | - | 1 | 0 | - | 0 | 0
8 | #DIV/0! | #DIV/0! | 2 | 0 | - | 2 | 0 | - | 0 | 0
9 | #DIV/0! | #DIV/0! | 3 | 0 | - | 3 | 0 | - | 0 | 0
10 | #DIV/0! | #DIV/0! | 4 | 0 | - | 4 | 0 | - | 0 | 0
11 | #DIV/0! | #DIV/0! | 5 | 0 | - | 5 | 0 | - | 0 | 0
12 | #DIV/0! | #DIV/0!
13 | #DIV/0! | #DIV/0! |  | Enclosure Type | a | k
14 | #DIV/0! | #DIV/0! |  | Panel/Enclosure | 100 | 0.127
15 | #DIV/0! | #DIV/0! |  | Switchboard | 400 | 0.312
16 | #DIV/0! | #DIV/0!
17 | #DIV/0! | #DIV/0! |  | Open Air
18 | #DIV/0! | #DIV/0! |  | Incident Energy | AFB
19 | #DIV/0! | #DIV/0! | 1 | #DIV/0! | #DIV/0!
20 | #DIV/0! | #DIV/0! | 2 | #DIV/0! | #DIV/0!
21 | #DIV/0! | #DIV/0! | 3 | #DIV/0! | #DIV/0!
22 | #DIV/0! | #DIV/0! | 4 | #DIV/0! | #DIV/0!
23 | #DIV/0! | #DIV/0! | 5 | #DIV/0! | #DIV/0!
24 | #DIV/0! | #DIV/0! | Total | - | -
25 | #DIV/0! | #DIV/0!
26 | #DIV/0! | #DIV/0! |  | Panel/Enclosure
27 | #DIV/0! | #DIV/0! |  | Incident Energy | AFB
28 | #DIV/0! | #DIV/0! | 1 | #DIV/0! | #DIV/0!
29 | #DIV/0! | #DIV/0! | 2 | #DIV/0! | #DIV/0!
|  |  | 3 | #DIV/0! | #DIV/0!
|  |  | 4 | #DIV/0! | #DIV/0!
|  |  | 5 | #DIV/0! | #DIV/0!
|  |  | Total | - | -
Switchboard
|  |  |  | Incident Energy | AFB
|  |  | 1 | #DIV/0! | #DIV/0!
|  |  | 2 | #DIV/0! | #DIV/0!
|  |  | 3 | #DIV/0! | #DIV/0!
|  |  | 4 | #DIV/0! | #DIV/0!
|  |  | 5 | #DIV/0! | #DIV/0!
|  |  | Total | - | -