Assets Planning and Delivery Group Engineering

DESIGN STANDARD DS 26-04

Type Specifications – Electrical

Type Specification for Large Cage Induction Motor

version 2 revision 1

March 2022

FOREWORD

The intent of Design Standards is to specify requirements that assure effective design and delivery of fit for purpose Water Corporation infrastructure assets for best whole-of-life value with least risk to Corporation service standards and safety. Design standards are also intended to promote uniformity of approach by asset designers, drafters and constructors to the design, construction, commissioning and delivery of water infrastructure and to the compatibility of new infrastructure with existing like infrastructure.

Design Standards draw on the asset design, management and field operational experience gained and documented by the Corporation and by the water industry generally over time. They are intended for application by Corporation staff, designers, constructors and land developers to the planning, design, construction and commissioning of Corporation infrastructure including water services provided by land developers for takeover by the Corporation.

Nothing in this Design Standard diminishes the responsibility of designers and constructors for applying the requirements of the Western Australia's Work Health and Safety (General) Regulations 2022 to the delivery of Corporation assets. Information on these statutory requirements may be viewed at the following web site location:

Overview of Western Australia’s Work Health and Safety (General) Regulations 2022 (dmirs.wa.gov.au)

Enquiries relating to the technical content of a Design Standard should be directed to the Senior Principal Engineer, Engineering. Future Design Standard changes, if any, will be issued to registered Design Standard users as and when published.

Head of Engineering

This document is prepared without the assumption of a duty of care by the Water Corporation.  The document is not intended to be nor should it be relied on as a substitute for professional engineering design expertise or any other professional advice.

Users should use and reference the current version of this document.

© Copyright – Water Corporation: This standard and software is copyright.  With the exception of use permitted by the Copyright Act 1968, no part may be reproduced without the written permission of the Water Corporation.

REVISION STATUS

The revision status of this standard is shown section by section below.

| REVISION STATUS |
| --- |
| SECT. | VER./REV. | DATE | PAGES REVISED | REVISION DESCRIPTION (Section, Clause, Sub-Clause) | RVWD. | APRV. |
| 1 | 1/5 | 30.08.11 | 8 | 1 revised | NHJ | AAK |
| 1 | 2/0 | 11.01.16 | 8 | 1 revised | NHJ | MSP |
| 3 | 2/0 | 11.01.16 | 10 | 3 revised | NHJ | MSP |
| 4 | 2/0 | 11.01.16 | 10 | 14 revised | NHJ | MSP |
| 6 | 2/0 | 11.01.16 | 12 | 6 revised | NHJ | MSP |
| 6 | 2/1 | 8.03.22 | 10 | 6 revised | SWG | EDG |
| 7 | 1/5 | 30.08.11 | 13 | 7 revised | NHJ | AAK |
| 7 | 2/0 | 11.01.16 | 13 | 7 revised and formatted | NHJ | MSP |
| 7 | 2/1 | 8.03.22 | 10 | 7 revised and formatted | SWG | EDG |
| 8 | 1/5 | 30.08.11 | 14 | 8 revised | NHJ | AAK |
| 8 | 2/0 | 30.11.15 | 14 | 8 revised | NHJ | MSP |
| 9 | 1/5 | 30.08.11 | 15 | 9 revised | NHJ | AAK |
| 10 | 1/5 | 30.08.11 | 16 | 10 revised | NHJ | AAK |
| 10 | 2/0 | 11.01.16 | 16 | 10 formatted | NHJ | MSP |
| 11 | 2/1 | 8.03.22 | 12 | 11 revised | SWG | EDG |
| 12 | 1/5 | 30.08.11 | 18 | 12 revised | NHJ | AAK |
| 13 | 1/5 | 30.08.11 | 19 | 13 revised | NHJ | AAK |
| 13 | 2/0 | 11.01.16 | 19 | 13 formatted | NHJ | MSP |
| 14 | 2/0 | 11.01.16 | 20 | 14 revised | NHJ | MSP |
| 15 | 2/0 | 11.01.16 | 21 | 15 revised | NHJ | MSP |
| 15 | 2/1 | 8.03.22 | 13 | 15.1 revised | SWG | EDG |
| 16 | 2/0 | 11.01.16 | 22 | 16 revised | NHJ | MSP |
| 17 | 2/0 | 11.01.16 | 23 | 16 revised | NHJ | MSP |
| 18 | 2/0 | 11.01.16 | 24 | 18 revised | NHJ | MSP |
| 19 | 2/0 | 11.01.16 | 25 | 19 revised | NHJ | MSP |
| 19 | 2/1 | 8.03.22 | 14 | 19 revised | SWG | EDG |
| 20 | 1/5 | 30.08.11 | 26 | 20.1, 20.4 revised | NHJ | AAK |
| 20 | 2/0 | 11.01.16 | 26 | 20 revised | NHJ | MSP |
| 21 | 1/5 | 30.08.11 | 27 | 21.5 revised | NHJ | AAK |
| 21 | 2/0 | 11.01.16 | 28 | 21 revised | NHJ | MSP |
| 21 | 2/1 | 8.03.22 | 15 | 21.1 formatter | SWG | EDG |
| 22 | 1/5 | 30.08.11 | 29 | 22.3 revised | NHJ | AAK |
| 22 | 2/0 | 11.01.16 | 30 | 22.3, 22.4, 22.5 revised | NHJ | MSP |
| 22 | 2/1 | 8.03.22 | 17-18 | 22.5 formatted | SWG | EDG |
| 23 | 2/0 | 11.01.16 | 31 | 23 revised | NHJ | MSP |
| 24 | 2/0 | 11.01.16 | 32 | 24 formatted | NHJ | MSP |
| 25 | 1/6 | 16.01.12 | 32 | Reformatted | KAW | NHJ |
| 25 | 2/0 | 11.01.16 | 33 | 25.1, 25.2 revised | NHJ | MSP |
| 28 | 2/0 | 11.01.16 | 35 | 28.4, 28.5 revised | NHJ | MSP |
| 28 | 2/1 | 8.03.22 | 20 | 28.5 formatted | SWG | EDG |
| 30 | 2/0 | 11.01.16 | 37 | 30 revised | NHJ | MSP |
| 32 | 2/1 | 8.03.22 | 21 | 32 formatted | SWG | EDG |
| 33 | 2/0 | 11.01.16 | 40 | 33 revised | NHJ | MSP |

| REVISION STATUS HISTORY |
| --- |
| VER./ REV. | DATE | PAGES REVISED | REVISION DESCRIPTION (Section, Clause, Sub-Clause) | RVWD. | APRV. |
| 0/0 | 01.0801 | All | New Edition | NHJ | AAK |
| 0/1 | 18.09.01 | 1 | 4.1,4.5 general revision | NHJ | AAK |
| 0/1 | 18.09.01 | 2 | 4.6,4.7 general revision | NHJ | AAK |
| 0/1 | 18.09.01 | 4 | 4.19.2 general revision | NHJ | AAK |
| 0/1 | 18.09.01 | 5 | 4.20.6 general revision | NHJ | AAK |
| 0/1 | 18.09.01 | 6 | 4.21.3,4.24.1 general revision | NHJ | AAK |
| 0/1 | 18.09.01 | 6 | 4.24.1 general revision | NHJ | AAK |
| 0/1 | 18.09.01 | 7 | 4.24.3,4.26.1 general revision | NHJ | AAK |
| 0/1 | 18.09.01 | 9 | 4.28,4.30 general revision | NHJ | AAK |
| 0/1 | 18.09.01 | 16 | 4.24.2 general revision | NHJ | AAK |
| 0/3 | 30.10.02 | 2 | 4.6 general revision | NHJ | AAK |
| 0/3 | 30.10.02 | 6 | 4.23 general revision | NHJ | AAK |
| 0/4 | 01.09.03 | All | Reformatted | NHJ | AAK |
| 0/4 | 01.09.03 | 1 | 4.1 general revision | NHJ | AAK |
| 0/4 | 01.09.03 | 3 | 4.14 general revision | NHJ | AAK |
| 0/4 | 01.09.03 | 4 | 4.20.1 general revision | NHJ | AAK |
| 0/4 | 01.09.03 | 6 | 4.24.1(c) general revision | NHJ | AAK |
| 0/4 | 01.09.03 | 11 | Annexure | NHJ | AAK |
| 1/0 | 27.02.04 | All | Section split | NHJ | AAK |
| 1/1 | 23.05.05 | All | Paragraphs renumbered | NHJ | AAK |
| 1/2 | 30.06.06 | 6 | 1 revised | NHJ | AAK |
| 1/3 | 30.04.07 | 7 | IEC 60034-15 added | NHJ | AAK |
| 1/3 | 30.04.07 | 10 | 20.4 added | NHJ | AAK |
| 1/4 | 02.06.08 | 6 | 1, 5 revised | NHJ | AAK |
| 1/4 | 02.06.08 | 7 | 7 revised | NHJ | AAK |
| 1/4 | 02.06.08 | 8 | 14 revised | NHJ | AAK |
| 1/4 | 02.06.08 | 9 | 19.1 revised | NHJ | AAK |
| 1/4 | 02.06.08 | 10 | 20.2, 20.3 revised | NHJ | AAK |
| 1/4 | 02.06.08 | 11 | 23, 24.1, 24.2 revised | NHJ | AAK |
| 1/4 | 02.06.08 | 14 | 30 revised | NHJ | AAK |

DESIGN STANDARD DS 26-04

Type Specifications – Electrical

Type Specification for Large Cage Induction Motor

CONTENTS

Section	Page

1	GENERAL	8

2	SITE	8

3	OPERATING MODE	8

4	WORK BY THE PRINCIPAL	8

5	INFORMATION FROM THE CONTRACTOR	9

6	CONTRACTOR’S DRAWINGS	9

7	STANDARDS	9

8	QUALITY ASSURANCE	10

9	POWER SUPPLY TO MOTOR	10

9.1	Directly Connected Motors	10

9.2	Low Voltage Motors for Converter Supply	10

9.3	High Voltage Motors for Converter Supply	11

10	MOTOR TYPE	11

11	MOTOR DUTY, NOMINAL FREQUENCY AND POWER RATING	11

12	TYPE OF LOAD	11

13	SYNCHRONOUS SPEED	12

14	DIRECTION OF ROTATION	12

15	COOLING	12

15.1	Type of Cooling (IC Code)	12

15.2	Air Ducts	12

15.3	Heat Exchanger	12

16	ENCLOSURE	13

17	TYPE OF CONSTRUCTION (IM CODE)	13

18	NOISE LEVEL	13

19	VIBRATION	13

20	TERMINATIONS	13

20.1	Type of Cable	13

20.2	High Voltage Terminations	13

20.3	Low Voltage Terminations	14

20.4	Termination of Cable Screens	14

20.5	Location of Cable Terminations	14

20.6	Separation	14

21	WINDINGS	14

21.1	General	14

21.2	Insulation Class	15

21.3	Winding Temperature Rise	15

21.4	H.V. Stator Lighting Impulse Withstand Voltage	15

21.5	Use with Converter Supply	15

21.6	High Voltage Motors in IEC 60034.25 Drives	16

21.7	Stator Control	16

22	BEARINGS	16

22.1	Lubricant	16

22.2	Bearing Loading	16

22.3	Power Frequency Circulating Currents	16

22.4	Common Mode Voltage Attenuation	16

22.5	Circulating Current Countermeasures	17

23	COUPLING	17

24	ANTI-CONDENSATION HEATING	17

25	PROTECTION	17

25.1	Winding Over Temperature Protection	17

25.2	Bearing Over Temperature Protection	18

25.3	Vibration Protection	18

26	PAINTING	18

27	MISCELLANEOUS REQUIREMENTS	18

27.1	Holding Down Bolts	18

27.2	Jacking Screws	19

27.3	Earthing Terminal	19

27.4	Lifting Eyes	19

28	WORKS TESTS	19

28.1	General	19

28.2	Efficiency Tests	19

28.3	Voltage Withstand Tests	19

28.4	Other Performance Tests	19

28.5	Routine Tests	19

29	DELIVERY AND INSTALLATION	20

30	ON SITE TESTING	20

31	AS-CONSTRUCTED INFORMATION	20

32	MANUALS	21

33	LIQUIDATED DAMAGES FOR LOW EFFICIENCY	21

# GENERAL

This Specification covers the requirements for the design, manufacture, assembly, inspection, factory testing, packaging, transport to site, on site assembly, on site testing, and commissioning of cage induction motors rated > 150 kW.

The motor shall be supplied to site complete with drive shaft coupling, all necessary accessories, miscellaneous material, minor parts and other such items necessary to complete assembly, testing and commissioning of the motor.

The installation and connection of the motor will be carried out by others in accordance with the Contractor’s instructions.

The Contractor shall return to site to commission the motor once the electrical and mechanical installation at the site has been completed.

# SITE

The motor will be housed in a weatherproof well ventilated building on the site, the location of which shall be as detailed in the Annexure.  Access to the site shall be as detailed in the Annexure.

# OPERATING MODE

The mode of operation for the motor shall be as detailed in the Annexure.

The operating environment shall be as detailed in the Annexure.

# WORK BY THE PRINCIPAL

- The Principal will supply and install the driven load machine including the bed plate for the motor.

- The Principal will install the motor on its bed plate, couple it to its load and connect it electrically.

- If air ducts are required as per clause 15.2, the Principal will supply air ducts and couplings of the size and type specified by the Contractor in his/her Tender Technical Response and will install such ducts.

- If a cooling water supply is required as per clause 15.3, the Principal will provide and connect a water supply to the motor at the pressure and flow rate specified by the contractor in his/her Tender Technical Response.

- Other work to be performed by the Principal shall be as detailed in the Annexure.

# INFORMATION FROM THE CONTRACTOR

The Contractor shall provide the following documentation in respect to the Motor at the times shown hereunder:

- General Arrangement Drawings including
certified mounted dimensions, and 
foundation loading diagram				28 days after date of order

- Final Design Equivalent Circuit Values		28 days prior to factory tests
(confirming values in the Contractor’s offer)

- Factory Test Certificates					within 7 days of the tests 
									and at least 7 days prior to 
									dispatch to site

- Operating & Maintenance Manual			On delivery

# CONTRACTOR’S DRAWINGS

The Contractor shall submit two A3 copies of the Contractor’s Drawings for approval.   The Contractor’s drawings shall show the general arrangement, material specifications, mounting dimensions and terminal connections.

All drawings submitted by the Contractor shall be in accordance with the latest issue of the relevant Australian Standards.

Adequate contrast shall be maintained between drawing detail and background, and the clarity and quality of the drawings shall be such as to enable the Principal to print and reproduce by clear and legible A3 copies for record purposes.

The drawings shall provide, in the title block, the number and title of the Contract, as well as details to identify the drawing, its contents, revision status and date of issue.

# STANDARDS

The workmanship, equipment and materials provided in accordance with this Specification shall comply in design, construction, rating and performance with the current relevant Australian Standards and Codes.

In their absence, compliance shall be with the relevant International Standards together with the requirements of competent Authorities having jurisdiction over all or any part of the design, manufacture, installation and operation of the equipment.

Specific reference is made within this Specification to the following Australian and International Standards:

AS 1359.102.1 	Rotating electrical machines - Methods of determining losses and efficiency - General

AS 1359.114 	Rotating electrical machines - Vibration measurement and limits

AS 2312		Guide to the protection of iron and steel against exterior atmospheric corrosion

AS 2729 		Roller bearings - Dynamic load rating life - Calculation methods

AS 60034.1		Rotating electrical machines - Rating and performance

AS 60034.5  	Rotating electrical machines - Degrees of protection provided by the integral design of rotating electrical machines (IP Code)

AS 60034.7		Rotating electrical machines - Classification of types of construction, mounting, arrangements and terminal position (IM Code)

AS 60034.8		Rotating electrical machines - Terminal markings and direction of rotation

AS 60034.9		Rotating electrical machines - Noise limits

AS/NZS ISO 9001 Quality management systems - Requirements

EN 50181		Plug-in type bushings above 1 kV up to 50 kV and from 250A to 2.5 kA for equipment other than liquid filled transformers

IEC 60034-6          Rotating electrical machines - Part 6: Methods of cooling (IC Code)

IEC 60034-15	Rotating electrical machines - Impulse voltage rating withstand levels of rotating A.C. machines with form wound stator coils

IEC 60034-18 	Rotating electrical machines - Functional evaluation of insulating systems

IEC 60034-25 	Rotating electrical machines - guidelines for the design and performance of A.C. motors specifically designed for converter supply.

IEC 60034-30-1 	Rotating electrical machines – Part 30-1: Efficiency classes of line operated AC motors (IE code).

IEC 60085		Electrical insulation - Thermal evaluation and designation

IEC 60751		Specifications for industrial platinum resistance thermometers and platinum sensors

ISO 9223 	Corrosion of metals and alloys - Corrosivity of atmospheres - Classification, determination and estimation

# QUALITY ASSURANCE

The motor shall be manufactured under a Quality System certified by an Accredited Authority to be in accordance with AS/NZS ISO 9001 or an approved equivalent.

# POWER SUPPLY TO MOTOR

## Directly Connected Motors

If the motor is specified in the Annexure to be connected directly to the mains, the motor shall be rated for operation from a three phase 50 Hz power supply having a solidly grounded neutral, a phase sequence of RWB and other characteristics as specified in the Annexure.

## Low Voltage Motors for Converter Supply

If the motor is specified in the Annexure as a Low Voltage motor for converter supply, the motor shall be rated for operation from a three phase variable frequency supply having a phase sequence of RWB and with the power drive system earthed at the associated Low Voltage supply transformer star connected winding neutral point.

The motor shall be rated for operation when being supplied with input voltages varying over the frequency range specified in the Annexure.

## High Voltage Motors for Converter Supply

If the motor is specified in the Annexure as a High Voltage motor for converter supply, the motor shall be rated for operation from a three phase variable frequency converter power supply having a phase sequence of RWB and with the power drive system earthed at the neutral of a common supply transformer if any, the middle point of a common D.C. bus, or the star point of an output sine filter, as specified in the Annexure.

The motor shall be rated for operation when being supplied with input voltages varying over the frequency range specified in the Annexure.

# MOTOR TYPE

- The motor shall be of the cage induction motor type in accordance with AS 60034.1.

- If the motor is specified in the Annexure to be connected directly to the mains, the motor shall be suitable for direct on line starting.

- In addition, if the motor is specified as a Low Voltage machine it shall be suitable for starting via a six wire electronic soft starter.

- If the motor is specified in the Annexure for converter supply, the motor shall be suitable for such duty (clauses 21.5 and 22.3 refer).

- For motors <185kW evidence shall be submitted on delivery that efficiency meets a minimum IE2 rating in accordance with IEC 60034-30-1 Table 5.

# MOTOR DUTY, NOMINAL FREQUENCY AND POWER RATING

- The motor duty shall be type S1 in accordance with AS 60034.1.

- The motor shall be designed for a nominal input supply frequency of either 50 Hz or 60 Hz as specified in the Annexure.

- The motor shall have a maximum power output rating at the nominal frequency as specified in the Annexure.  This rating shall be at the above duty rating and shall be under the specified operating conditions.

# TYPE OF LOAD

- The motor shall be suitable for driving the type of load specified in the Annexure.

- If the motor is specified for converter supply, the motor shall have an output power versus frequency rating not less than the output power versus frequency requirement specified in the Annexure

# SYNCHRONOUS SPEED

The motor’s synchronous speed at the specified nominal frequency shall be as specified in the Annexure.

# DIRECTION OF ROTATION

The motor’s direction of rotation in accordance with AS 60034.8 shall be as specified in the Annexure.

# COOLING

## Type of Cooling (IC Code)

The type of cooling used shall be one of the following IEC 60034-6 classifications as specified in the Annexure:

- IC0A1, i.e. air as primary coolant circulated with a motor shaft driven fan from, and back to, the surrounding air,

- IC2A1, i.e. air as primary coolant with a motor shaft driven fan drawing air directly from surrounding air and discharging outside the pump station via an outlet duct

- IC3A1, i.e. air as primary coolant with a motor shaft driven fan drawing air from outside the pump station and delivering air to a different location outside the pump station via inlet and outlet ducts.

- IC8A1W7, i.e. air as primary coolant and water as secondary coolant with a motor mounted heat exchanger, the air being circulated by a motor shaft driven fan and the water being moved by means separate from the motor

## Air Ducts

- If the type of cooling is specified in the Annexure as IC2A1, the required length of the above outlet duct as per clause 14.1(b) shall be as shown in the Annexure.

- If the type of cooling is specified in the Annexure as IC3A1, the required length of the above inlet and outlet ducts as per clause 14.1(c) shall be as shown in the Annexure.

## Heat Exchanger

If the type of cooling is specified in the Annexure as IC8A1W7:

- The hydraulic resistance of the water circuit within the air/water heat exchanger shall be such that at the required maximum flow rate specified by the Contractor in his/her Tender Technical Response, the pressure drop across the heat exchanger shall be not more than the value specified by the Contractor in his/her Tender Technical Response,

- The heat exchanger shall be provided with detection equipment to trip the motor out on fault should a water leak occur, and

The water circuit within the heat exchanger shall be constructed of materials which will not suffer corrosion if used with water having the chemical composition specified in the Annexure.

# ENCLOSURE

- If the type of cooling is specified as IC0A1 or IC2A1:

(i)	the motor shall be of drip proof construction and shall be protected to AS 60034.5 classification IP22, and

(ii)	the motor shall have no ventilation openings in the drive end face of the enclosure, so that spray from a leaking pump seal cannot enter the motor directly.

- If the type of motor cooling is specified as IC3A1 or IC8A1W7 the motor shall be of totally closed construction and shall be protected to AS 60034.5 classification IP56.

# TYPE OF CONSTRUCTION (IM CODE)

The motor type of construction and mounting shall be of the AS 60034.7 classification specified in the Annexure.

# NOISE LEVEL

The motor shall be fitted with low noise unidirectional cooling fan and other noise limiting devices. Unless a lower noise level is specified in the Annexure, the emitted noise level shall be at least 12 dB below the relevant value quoted in Table 1 of the AS 60034.9.

# VIBRATION

The motor shall be designed and constructed so that the vibration severity level under rigid mounting conditions shall not exceed vibration grade R over the frequency range 10 Hz to 1 kHz in accordance with AS 1359.114. The works test shall be conducted with a half key fitted.

# TERMINATIONS

## Type of Cable

The type and size of stator cables shall be as specified in the Annexure.

## High Voltage Terminations

- High Voltage stator windings shall be fitted with the EN 50181 Type A or Type C High Voltage terminal bushings suitable for High Voltage, cold fit, fully screened, dead-break elbow connectors; so as to allow the termination of High Voltage single core XLPE insulated cables with light duty screens.

The High Voltage cable terminations shall be located within a bolted or locked steel enclosure fitted on the front with an aluminium warning label engraved as follows:

CAUTION

DEAD-BREAK ELBOWS

DO NOT CONNECT OR DISCONNECT LIVE

- Alternatively, High Voltage stator windings shall be terminated in fully enclosed steel cable boxes with DIN, CENELEC or ANSI standard bushings which are suitable for use with cold fit insulating boots.

## Low Voltage Terminations

If the motor is to be supplied with a Low Voltage stator winding, the terminations shall be in a metal terminal box fitted with a non-ferrous gland plate and sized so as to provide adequate space for the termination of the stator cables specified in the Annexure.  The stator terminal box shall be rated to withstand an internal arcing fault without danger to nearby personnel or damage to adjacent plant.

Similarly, the stator terminal box shall be rated to withstand without damage the forces due to a motor short circuit under site conditions.

## Termination of Cable Screens

Terminal boxes on motors specified for converter supply and for which screened stator cables have been specified in the Annexure shall be provided with cable glands which provide concentric termination of cable screens.

## Location of Cable Terminations

The location of cable terminations shall be as specified in the Annexure.

## Separation

Separate terminal boxes shall be provided for auxiliary circuits such as anti-condensation heaters, winding temperature sensors, etc.

# WINDINGS

## General

The motor windings shall:

- Be form wound

- Be designed to have an even temperature distribution free from hot spots

- Be suitably braced to give adequate rigidity under short circuit and starting conditions

- Be vacuum impregnated with suitable insulating varnish to render them damp proof and oil resistant

## Insulation Class

The winding system shall have been developed on the basis of functional evaluation in accordance with IEC 60034.18.  Winding insulation shall not be less than IEC 60085 Class F.

## Winding Temperature Rise

The winding temperature rise at maximum power output rating shall not exceed the temperature rise limits specified in AS 60034.1 for IEC 60085 class B insulation.

## H.V. Stator Lighting Impulse Withstand Voltage

If the motor is a High Voltage motor, the stator winding lightning impulse withstand voltage rating shall be not less than the value specified in IEC 60034.15 (i.e. 4 times the stator voltage plus 5 kV).

## Use with Converter Supply

- If the motor is specified in the Annexure as a Low Voltage machine suitable for supply from a converter supply, the motor shall comply with the requirements of clauses 21.5 (b) to 21.5(d) hereunder.

- The motor windings shall be such that the motor is suitable for incorporation into a power drive system having its earthing connection at any one of the following locations as specified in the Annexure:

(i)  	at the neutral of an incoming isolating transformer,

(ii) 	at the middle point of a D.C. bus, or

(iii) 	at the star point of an output phase to earth sine filter (if the latter is provided).

- Motor windings on motors rated at < 440 volts shall have phase to phase impulse voltage ratings greater than those specified Figure 14 Curve A of IEC 60034.25.

Unless such motors are specified in the Annexure to be supplied from converters fitted with common mode voltage filtering, the winding phase to earth impulse voltage ratings shall be not less than twice these values.

- Motor windings on motors rated at > 440 < 690 volts shall have phase to phase impulse voltage ratings greater than those specified Figure 14 Curve B of IEC 60034.25.

Unless such motors are specified in the Annexure to be supplied from converters fitted with common mode voltage filtering, the winding phase to earth impulse voltage ratings shall be not less than twice these values.

- If the motor is specified in the Annexure as a High Voltage machine suitable for supply from a non-specific converter supply, the motor windings shall be suitable for supply to the motor from a converter which incorporates sinusoidal phase to phase output voltage filtering and common mode voltage filtering, with star point of the filters being earthed.

## High Voltage Motors in IEC 60034.25 Drives

- If the motor is specified in the Annexure as a High Voltage machine being supplied by the Contractor as part of an overall power drive system which includes a variable speed controller, motor, cabling and installation, the motor windings shall be designed for supply from the particular converter in accordance with the requirements of IEC 60034.25.

- Windings in High Voltage IEC 60034.25 rated motors shall have dV/dt and impulse voltage ratings in accordance with the values specified in the Contractor’s Technical Tender Response Schedule.

## Stator Control

- If the motor is specified to be supplied directly from the incoming mains the motor shall be suitable for control via the switching device specified in the Annexure.

- If the above switching device is specified as being a vacuum contactor, the motor stator shall be provided with additional turn to turn insulation as a minimum precaution.

# BEARINGS

## Lubricant

Bearings shall be of the rolling element construction and shall be grease lubricated.  The grease used shall be lithium based mineral oil grease, “Shell Alvania EPLF2” or equivalent.

The bearing housings shall be fitted with grease nipples and automatic grease pressure relief and venting systems.

## Bearing Loading

The bearing system shall be capable of carrying enough axial load to allow the motor to be run disconnected from the load.

The motor shall be fitted with bearings having a rated operating life in accordance with AS 2729 of 100,000 hours under the specified operating conditions.

## Power Frequency Circulating Currents

The motor shall be supplied with insulated non drive end bearings regardless of whether it is specified for converter supply or not, so as to provide protection against bearing damage caused by power frequency circulating currents.

## Common Mode Voltage Attenuation

- If the motor is specified in the Annexure as being supplied separately, i.e. in accordance with clause 21.5, no further countermeasures shall need to be taken in order to prevent bearing damage due to high frequency circulating currents.

- Similarly, if the motor is specified in the Annexure as being supplied as part of an overall power drive system, and the Contractor provides the associated variable speed controller with common mode voltage attenuation, no further countermeasures shall need to be taken in order to prevent bearing damage due to high frequency circulating currents.

## Circulating Current Countermeasures

- If the variable speed controller is not to be fitted with common mode voltage attenuation in accordance with clause 22.4 above, the motor shall be provided with all the following countermeasures against bearing damage due to high frequency circulating currents:

(i)	An insulated drive end bearing, in addition to the insulated non-drive end bearing required in accordance with clause 22.3 above

(ii)	An insulated drive shaft coupling

(iii)	A shaft grounding ring

- The shaft grounding ring shall be an AEGIS type iPRO, or similar approved, and shall:

(i)	Incorporate at least four circumferential rows of conductive micro-fibres

(ii)	Limit the shaft to ground voltage to less than 4 volts

(iii)	Be virtually maintenance free, i.e. have a rated life of not less than 100,000 hours

# COUPLING

- The Contractor shall fit the drive end half coupling to the motor shaft and shall ensure that the combination is balanced correctly.

- The Contractor shall supply the Principal with the driven side half coupling, bored to suit the shaft diameter advised by the Principal and balanced with a half key fitted.

# ANTI-CONDENSATION HEATING

The motor shall be fitted with in built anti-condensation heaters rated to raise the temperature of the motor 4oC above ambient with the motor de-energised and the heaters on.

Anti-condensation heaters shall be suitable for operation from a single phase 50 Hz power supply with an operating voltage of 240 volts.

Anti-condensation heaters shall be suitable for supply via a 30 mA Residual Current Device.

A label carrying the following warning shall be fitted in the vicinity of the anti-condensation heater terminal box:

CAUTION

THE MOTOR ANTI-CONDENSATION HEATER IS “ON” WHEN THE MOTOR

IS “OFF”

# PROTECTION

## Winding Over Temperature Protection

- The motor stator windings shall be fitted with over temperature protection either in the form of Resistance Temperature Detectors (RTD’s) embedded in the windings or thermistors embedded in the windings.

- If RTD’s are supplied these shall be three wire platinum element type having Grade B accuracy in accordance with IEC 60751 and shall have a resistance of 100 ohms at 0oC with a fundamental interval of 38.50 ohms.

Two RTD’s shall be embedded within each phase winding and all RTD’s shall be brought out separately via suitably protected leads so that one set of RTD’s can be used for winding temperature indication and protection and the other set retained as spare.

- If thermistor protection is supplied, a single P.T.C. thermistor shall be supplied embedded in the end turns of each phase winding. The trip temperature shall be in accordance with the manufacturer’s recommended practice and the temperature – resistance characteristic shall be such that the resistance of each thermistor at trip temperature is 1000 ohms.  The connections to each thermistor shall be brought out separately via suitably protected leads.

## Bearing Over Temperature Protection

The motor shall have a thermometer pocket complete with a Resistance Temperature Detector (RTD) in each bearing housing.  RTD’s shall be three wire platinum element type having Grade B accuracy in accordance with IEC 60751 and shall have a resistance of 100 ohms at 0oC with a fundamental interval of 38.50 ohms.  The RTD’s shall be brought out separately via suitably protected leads.  Bearing RTD leads may be terminated in the same terminal box as winding RTD’s if these are fitted but shall be kept separate from other circuits.

## Vibration Protection

The motor shall be fitted with vibration protection only if this is specified in the Annexure.

Vibration protection shall be of the rigidly affixed permanently connected accelerometer type.  An accelerometer shall be fixed, in a readily accessible location, directly in contact with each bearing housing.

Cabling from accelerometer to the associated preamplifier shall be of the low noise type and the preamplifier shall be mounted on the motor adjacent to the RTD terminal box.

# PAINTING

A paint coating which is rated in accordance with AS 2312 (and ISO 9223) to provide Long Term Protection to steel in industrial environments shall be applied to the motor.

# MISCELLANEOUS REQUIREMENTS

## Holding Down Bolts

If the motor is to be one of a group of similar motors, holes for holding down bolts or set screws and cable terminations shall be drilled to a common template to facilitate interchangeability of motors.  The drilling templates shall be such that the location of holes relative to the motor centre line remains constant from motor to motor.

## Jacking Screws

If the motor has been specified in the Annexure as foot mounted, jacking screws shall be provided at each motor foot in order to facilitate leveling of the machine prior to installation of necessary shims and final bolting down.

The combined motor/load machine base plate will be supplied and installed by the Principal in accordance with the certified mounting dimensions provided by the Contractor.

## Earthing Terminal

An external motor earthing terminal shall be provided in an accessible position close to the stator termination.

## Lifting Eyes

A minimum of two lifting eyes rated for the weight of the fully assembled motor shall be provided.

# WORKS TESTS

## General

The Contractor shall submit the motor to works tests as detailed hereunder and shall provide the Principal with certified test certificates including the actual test result recorded.

The Contractor shall make provision for such tests to be witnessed if witnessed testing is specified in the Annexure.

## Efficiency Tests

The motor shall undergo testing of motor efficiency by the summation of losses in accordance with AS 1359.102.1 at 50% load, at 75% load and at 100% load.

## Voltage Withstand Tests

The motor shall be submitted to voltage withstand tests in accordance with AS 60034.1.

## Other Performance Tests

The motor shall be submitted to testing in accordance with a recognized national standard to substantiate all of the performance values included in the Contractor’s tender.

## Routine Tests

Routine Check Tests shall be defined as those tests which need to be applied to the machine to show that it is able to withstand the appropriate voltage withstand tests and is in correct working order both electrically and mechanically.

All motors shall be subjected to Routine Check Tests at the manufacturer’s works.

Routine Check Tests shall include the following:

- Winding resistance measurement

- Windings insulation resistance measurement at not less than 500 volts for Low Voltage machines and not less than 1000 volts for High Voltage machines

- Air gaps measurement

- Voltage withstand tests in accordance with AS 60034.1

- An additional high voltage test at 120% of the test voltage specified in AS 60034.1 for 10 seconds (only for motors to be controlled by vacuum contactors)

- Confirmation of terminal markings and direction of rotation

- No load tests at rated voltage recording volts, amps, and kilowatts

- No load vibration test

# DELIVERY AND INSTALLATION

The Contractor shall deliver, unload, unpack and assemble as necessary the complete motor at the site.

The Contractor shall inspect the unpacked motor and shall ensure that the motor is undamaged.

The Contractor shall give the Principal seven days’ notice of when the motor will be ready for installation onto the bed plate and coupled to the driven load.  The installation, alignment and coupling shall be completed by the Principal in the presence of the Contractor and to the Contractor’s satisfaction.

# ON SITE TESTING

Before the Contractor makes the motor available to the Principal for connection to the electrical system, the Contractor shall carry out the following tests:

- Insulation resistance test

- Reduced voltage withstand test

The Contractor shall supply all equipment, materials and labour for such testing and shall make the results of such tests available to the Principal at the time that the motor is made available for connection to the electricity supply.

# AS-CONSTRUCTED INFORMATION

The Contractor shall provide As-Constructed information on all drawings.  As-Constructed drawings shall be provided electronically with A3 size hard copies.

# MANUALS

The Contractor shall supply three copies of comprehensive instruction manuals, written in English and covering the complete operation and maintenance requirements of all equipment supplied under the Contract.

The manuals shall be printed on high grade A4 size paper and shall be bound in a high grade A4 size loose leaf binder.

Information included in the manuals shall include:

- Operating instructions

- Safety instructions and warnings

- Maintenance instructions and schedules

- Recommended spare parts and special tool list

- As-constructed drawings

- Detailed equipment performance specifications

- Test reports and certificates

# LIQUIDATED DAMAGES FOR LOW EFFICIENCY

In addition to any liquidated damages specified in the general conditions of contract, the Contractor shall be liable to the Principal for liquidated damages in respect of failure of the motor to achieve the level of full load efficiency quoted previously in the Tender Technical Response Schedule.

Such liquidated damages shall be calculated on the basis of capitalised cost of losses as specified in the Annexure and on the basis that losses in excess of the quoted value plus the tolerance allowed in AS1359.102.1.

Annexure to Specification

for

Large Cage Induction Motor

Project:

Drive Title (e.g. No. 1 North Pump):

Form of Contract:

Purchased as part of complete power drive system (yes or no):

Site Location (clause 2 refers):

Type of Access to Site:

Operating Mode (Clauses 3, 12 refers)

Type of Load (i.e. pump, fan etc.)

Type of drive (i.e. fixed or variable speed drive)

Motor supply (i.e. mains, or PWM VSC – converter)

Drive maximum speed	 rpm

Drive minimum speed (if VSD) 	 rpm

Load at maximum speed 	 kW

Load at minimum speed (if VSD) 	 kW

Type of Starter (if not VSD)

Estimated annual running time 	 hrs

Motor direction of rotation

Annexure to Specification

Operating Environment

Maximum ambient temperature:		oC

Minimum ambient temperature:		oC

Maximum Ambient Air Relative Humidity:		%

Ambient Air Borne Contaminants:

Work to be Done by Principal (Clause 4 refers)

Power Supply to Mains Connected Motor (Clause 9.1 refers)

Frequency tolerance	  %

Phase to phase voltage 	 V

Voltage tolerance (long term) 	%

Impedance of electrical supply system to motor  	+  j 	ohm

Location of supply earthing connection

Power Supply to Converter Connected Motor (Clauses 9.2, 9.3, 10, 21.5, 21.6 refers)

Maximum output frequency 	 Hz

Minimum output frequency 	 Hz

Output voltage at maximum output frequency 	 V

Maximum output current 	 amps

Position of power drive system earth

H.V. motor/converter as IEC 60034.25 set (yes or no)

Sinusoidal phase to phase voltage output filtered (yes or no)

Output common mode voltage filtered (yes or no)

Annexure to Specification

Motor Rated Characteristics (Clauses 11, 13 and 14 refers)

Motor rated frequency 	 Hz

Motor rated speed 	r.p.m.

Motor rated voltage 	V

Motor rated S1 output power 	kW

Maximum locked rotor current 	 amps

Minimum locked rotor torque 	 newton metres

Minimum pull up torque 	 newton metres

Minimum breakdown torque 	 newton metres

Motor direction (facing DE)

Motor Efficiency Rating 	IE

Type of Cooling (Clause 15 refers)

IEC 60034-6  designation 	 IC

Range of coolant temperature at motor inlet 	oC  to 	oC

Cooling Water Chemical Composition

Sodium 	mg/1
	Potassium 	mg/1

Magnesium	mg/1
	Calcium	mg/1

Bicarbonate 	mg/1
	Sulphate 	mg/1

Chloride 	mg/1
	Nitrate 	mg/1

Carbonate 	mg/1
	Silica 	mg/1

Total Soluble Salts	mg/1
	Iron 	mg/1

Total hardness 	mg/1

Alkalinity (as Ca C03)	mg/1	pH

Type of Construction and Mounting (Clause 17 refers)

AS 60034.7 designation 	IM

Mounting holes drilled to a common template (required or not)

Annexure to Specification

Noise Level

Special low noise level design (required or not)

If required, maximum no load sound power level 	 dBA

Stator Cable (Clause 20 refers)

Number of cores

Type of Construction

Insulation type

Conductor material

Conductor size 	sq mm

Screen type (if applicable)

IEC 600034.25 Supply (Clause 21.6, 22.45 refers)

To be supplied as part of a complete overall power drive system (yes or no)

Stator Control Switching Device (Clause 21.7 refers)

Type

Make and Model

Vibration Protection (Clause 25.3 refers)

Vibration protection (required or not)

Tests (Clause 28.1 refers)

Witnessed tests (required or nor)

Liquidated Damages for Low Efficiency (Clause 33 refers)

Capitalised costs of losses 	$/kW

| Type Specification for Large Cage Induction Motor Tender Technical Response Schedule |
| --- |
| Clause | Subject | Noted | Compliance | Comments |
| No. |  |  | Yes | No |  |
| 1. | General |  |  |  |  |
| 2. | Site |  |  |  |  |
| 3. | Operating Mode |  |  |  | Mains characteristics: |
|  |  |  |  |  | Offer motor efficiency % at 0.5 load = |
|  |  |  |  |  | Offer motor efficiency % at 0.75 load = |
|  |  |  |  |  | Offer motor efficiency % at full load = |
|  |  |  |  |  | Offer motor power factor at 0.5 load = |
|  |  |  |  |  | Offer motor power factor at 0.75 load = |
|  |  |  |  |  | Offer motor power factor at full load = |
|  |  |  |  |  | Offer allowable max. rpm = |
|  | Operating Environment |  |  |  |  |
| 4. | Work by Principal |  |  |  |  |
| 5. | Information from Contractor |  |  |  |  |
|  | Equivalent Circuit Values |  |  |  | Offer stator resistance ohms = |
|  | (Referred to stator) |  |  |  | Offer stator reactance ohms =- |
|  |  |  |  |  | Offer rotor resistance ohms = |
|  |  |  |  |  | Offer rotor reactance ohms = |
|  |  |  |  |  | Offer magnetizing conductance mhos = |
|  |  |  |  |  | Offer magnetizing susceptance mhos = |
|  |  |  |  |  | Offer turns ratio = |
| 6. | Contractor’s Drawings |  |  |  |  |
| 7. | Standards |  |  |  |  |
| 8. | Quality Assurance |  |  |  |  |
| 9. | Power Supply to Motor |  |  |  |  |
| 9.1 | Directly Connected Motor |  |  |  |  |
| 9.2 | L.V. Motors for Converter Supply |  |  |  | Offer 50 Hz rated kV = |
| 9.3 | H.V. Motors for Converter Supply |  |  |  |  |
| 10. | Motor Type |  |  |  |  |
|  |  |  |  |  | Offer stator star or delta connected? |
|  |  |  |  |  | Motor Efficiency Rating = |
| 11. | Motor Duty, Nominal Frequency & Power Rating |  |  |  | Offer nominal Hz = |
|  |  |  |  |  | Mains Characteristics at nominal Hz: |
|  |  |  |  |  | Offer duty type = |
|  |  |  |  |  | Offer rated kW = |
|  |  |  |  |  | Offer stator rated kV = |
|  |  |  |  |  | Offer stator rated FLC amps = |
|  |  |  |  |  | (Offer speed current curve to be attached) |
|  |  |  |  |  | Offer locked rotor torque Nm = |
| Type Specification for Large Cage Induction Motor Tender Technical Response Schedule |
| Clause | Subject | Noted | Compliance | Comments |
| No. |  |  | Yes | No |  |
|  |  |  |  |  | Offer pull up torque Nm = |
|  |  |  |  |  | Offer breakdown torque Nm = |
|  |  |  |  |  | (Offer speed torque curve to be attached) |
| 12. | Type of Load |  |  |  |  |
| 13. | Synchronous Speed |  |  |  | Offer synchronous r.p.m. = |
| 14. | Direction of Rotation |  |  |  |  |
| 15. | Cooling |  |  |  |  |
| 15.1 | Type of Cooling |  |  |  | Offer IC Code = |
| 15.2 | Air Ducts |  |  |  | Offer outlet duct m = |
|  |  |  |  |  | Offer inlet duct m = |
| 15.3 | Heat Exchanger |  |  |  | Offer requirement |
|  |  |  |  |  | Inlet pressure m = |
|  |  |  |  |  | Flow rate e/s = |
|  |  |  |  |  | Offer material used in water circuit – attach details |
| 16. | Enclosure (IP Code) |  |  |  | Offer IP rating = |
| 17. | Type of Construction (IM Code) |  |  |  | Offer IM rating = |
|  |  |  |  |  | Offer overall weight kg = |
|  |  |  |  |  | Offer rotor weight kg = |
|  |  |  |  |  | Offer shaft diam. mm = |
|  |  |  |  |  | Offer height to shaft centerline metres = |
|  |  |  |  |  | Offer overall height metres = |
|  |  |  |  |  | Offer overall length metres = |
|  |  |  |  |  | Offer overall width metres = |
| 18. | Noise Level |  |  |  | Offer noise power dBA = |
| 19. | Vibration Level |  |  |  | Offer vibration mm/s rms |
| 20. | Terminations |  |  |  |  |
| 20.1 | Type of Cable |  |  |  |  |
| 20.2 | High Voltage Terminations |  |  |  |  |
| 20.3 | Low Voltage Terminations |  |  |  | Fault rating kA = |
| 20.4 | Termination of Cable Screens |  |  |  |  |
| 20.5 | Location of Terminations |  |  |  |  |
| 20.6 | Separation |  |  |  |  |
| 21. | Windings |  |  |  |  |
| 21.1 | General |  |  |  |  |
| 21.2 | Insulation Class |  |  |  | Offer IEC 60085 class = |
| 21.3 | Winding Temperature Rise |  |  |  | Offer temp rise degree C = |
| 21.4 | Stator L.I.W.V. |  |  |  | Offer stator L.I.W.V. kV = |
| Type Specification for Large Cage Induction Motor Tender Technical Response Schedule |
| Subject | Noted | Compliance | Comments |
|  |  | Yes | No |  |
| 21.5 | Use with Converter Supply |  |  |  |  |
| 21.6 | H.V. Motors in IEC 60034.25 drives |  |  |  | Winding rated dV/dt, kV/µs = Winding rated impulse volts, kV = |
| 21.7 | Stator Control |  |  |  |  |
| 22. | Bearings |  |  |  |  |
| 22.1 | Type and grade of bearing lubricant |  |  |  |  |
|  |  |  |  |  | Regreasing interval running hrs = |
| 22.2 | Bearing loading |  |  |  |  |
|  |  |  |  |  | Offer ball bearing nominal life hrs = |
|  |  |  |  |  | Offer roller bearing design load factor |
|  |  |  |  |  | Offer ball bearing design load factor = |
| 22.3 | Power Frequency Circulating Current |  |  |  |  |
| 22.4 | Common Mode Voltage Attenuation |  |  |  |  |
| 22.5 | Circulating Current Countermeasures |  |  |  | Shaft grounding ring:- No. conductive fibre rows = Rated life, hrs = Max shaft to ground, volts = |
| 23. | Coupling |  |  |  |  |
| 24. | Anti-Condensation Heating |  |  |  |  |
|  |  |  |  |  | Offer motor temp. rise degrees C = |
|  |  |  |  |  | Offer heaters rated Volts = |
|  |  |  |  |  | Offer heaters rated Amps = |
| 25. | Protection |  |  |  |  |
| 25.1 | Winding O/Temp Protection |  |  |  | Type O.T. protection offered = |
| 25.2 | Bearings O/Temp Protection |  |  |  |  |
| 25.3 | Vibration Protection |  |  |  | (Details of proposal to be attached) |
| 26. | Painting |  |  |  | Offer paint DFT microns = |
| 27. | Miscellaneous Requirements |  |  |  |  |
| 27.1 | Holding Down Bolts |  |  |  |  |
| 27.2 | Jacking Screws |  |  |  |  |
| 27.3 | Earthing Terminal |  |  |  |  |
| 27.4 | Lifting Eyes |  |  |  |  |
| 28. | Work Tests |  |  |  |  |
| 28.1 | General |  |  |  |  |
| 28.2 | Efficiency Tests |  |  |  |  |
| 28.3 | Voltage Withstand Tests |  |  |  |  |
| 28.4 | Other Performance Tests |  |  |  | (Details of proposal to be attached) |
| 28.5 | Routine Check Tests |  |  |  | (Details of proposal to be attached) |
|  | Availability of Type Tests |  |  |  | Currently available, yes or no? |
| Type Specification for Large Cage Induction Motor Tender Technical Response Schedule |
| Subject | Noted | Compliance | Comments |
|  |  | Yes | No |  |
| 29. | Delivery and Installation |  |  |  |  |
| 30. | On Site Testing |  |  |  |  |
| 31. | As Constructed Information |  |  |  |  |
| 32. | Manuals |  |  |  |  |
| 33. | Liquidated Damages |  |  |  |  |

END OF DOCUMENT