Assets Planning and Delivery Group

Engineering

DESIGN STANDARD DS 26-18

Type Specification – Electrical

Type Specification for Large Variable Speed Controllers without Input Isolating Transformers

VERSION  3

REVISION  1

SEPTEMBER 2022

FOREWORD

The intent of Design Standards is to specify requirements that assure effective design and delivery of fit for purpose Water Corporation infrastructure assets for best whole-of-life value with least risk to Corporation service standards and safety. Design standards are also intended to promote uniformity of approach by asset designers, drafters and constructors to the design, construction, commissioning and delivery of water infrastructure and to the compatibility of new infrastructure with existing like infrastructure.

Design Standards draw on the asset design, management and field operational experience gained and documented by the Corporation and by the water industry generally over time. They are intended for application by Corporation staff, designers, constructors and land developers to the planning, design, construction and commissioning of Corporation infrastructure including water services provided by land developers for takeover by the Corporation.

Nothing in this Design Standard diminishes the responsibility of designers and constructors for applying the requirements of WA WHS General Regulations 2022 (Part 6.2 – Duties of designer of structure and person who commissions construction work) to the delivery of Corporation assets. Information on these statutory requirements may be viewed at the following web site location:

https://www.legislation.wa.gov.au/legislation/statutes.nsf/law_s53267.html

Enquiries relating to the technical content of a Design Standard should be directed to the Senior Principal Engineer - Electrical, Engineering. Future Design Standard changes, if any, will be issued to registered Design Standard users as and when published.

Head of Engineering

This document is prepared without the assumption of a duty of care by the Water Corporation.  The document is not intended to be nor should it be relied on as a substitute for professional engineering design expertise or any other professional advice.

Users should use and reference the current version of this document.

© Copyright – Water Corporation: This standard and software is copyright.  With the exception of use permitted by the Copyright Act 1968, no part may be reproduced without the written permission of the Water Corporation.

DISCLAIMER

Water Corporation accepts no liability for any loss or damage that arises from anything in the Standards/Specifications including any loss or damage that may arise due to the errors and omissions of any person. Any person or entity which relies upon the Standards/Specifications from the Water Corporation website does so that their own risk and without any right of recourse to the Water Corporation, including, but not limited to, using the Standards/Specification for works other than for or on behalf of the Water Corporation.

The Water Corporation shall not be responsible, nor liable, to any person or entity for any loss or damage suffered as a consequence of the unlawful use of, or reference to, the Standards/Specifications, including but not limited to the use of any part of the Standards/Specification without first obtaining prior express written permission from the CEO of the Water Corporation.

Any interpretation of anything in the Standards/Specifications that deviates from specific Water Corporation Project requirements must be referred to, and resolved by, reference to and for determination by the Water Corporation’s project manager and/or designer for that particular Project.

REVISION STATUS

The revision status of this standard is shown section by section below

| REVISION STATUS |
| --- |
| SECT. | VER./REV. | DATE | PAGES REVISED | REVISION DESCRIPTION (Section, Clause, Sub-Clause) | RVWD. | APRV. |
| All | 2/0 | 30.08.11 | All | New Version | NHJ | AAK |
| C Page | 3/0 | 12.01.16 | 1 | New Version | NHJ | MSP |
| TOC | 3/0 | 12.01.16 | 6 | New Version | NHJ | MSP |
| 1 | 3/0 | 12.01.16 | 9 | New Version | NHJ | MSP |
| 3 | 3/0 | 12.01.16 | 11 | New Version | NHJ | MSP |
| 5 | 3/0 | 12.01.16 | 13 | New Version | NHJ | MSP |
| 6 | 3/0 | 12.01.16 | 14 | New Version | NHJ | MSP |
| 7 | 3/0 | 12.01.16 | 15 | New Version | NHJ | MSP |
| 8 | 3/0 | 12.01.16 | 16/17 | New Version | NHJ | MSP |
| 11 | 3/0 | 12.01.16 | 20 | New Version | NHJ | MSP |
| 12 | 3/0 | 12.01.16 | 21 | New Version | NHJ | MSP |
| 13 | 3/0 | 12.01.16 | 22 | New Version | NHJ | MSP |
| 14 | 3/0 | 12.01.16 | 23 | New Version | NHJ | MSP |
| 15 | 3/0 | 12.01.16 | 24 | New Version | NHJ | MSP |
| 16 | 3/0 | 12.01.16 | 25 | New Version | NHJ | MSP |
| 17 | 3/0 | 12.01.16 | 26 | New Version | NHJ | MSP |
| 18 | 3/0 | 12.01.16 | 27 | New Version | NHJ | MSP |
| 19 | 3/0 | 12.01.16 | 28/29/30 | New Version | NHJ | MSP |
| 20 | 3/0 | 12.01.16 | 31/32/33 | New Version | NHJ | MSP |
| 22 | 3/0 | 12.01.16 | 36 | New Version | NHJ | MSP |
| 25 | 3/0 | 12.01.16 | 39 | New Version | NHJ | MSP |
| 26 | 3/0 | 12.01.16 | 40 | New Version | NHJ | MSP |
| Annexure | 3/0 | 12.01.16 | 50 to 57 | New Version | NHJ | MSP |

| REVISION STATUS HISTORY |
| --- |
| VER./ REV. | DATE | PAGES REVISED | REVISION DESCRIPTION (Section, Clause, Sub-Clause) | RVWD. | APRV. |
| 0/3 | 30.10.02 | All | New section | NHJ | AAK |
| 0/4 | 01.09.03 | All | Reformatted | NHJ | AAK |
| 0/4 | 01.09.03 | 2 | 19.9 general revision | NHJ | AAK |
| 1/0 | 27.02.04 | All | Sections split | NHJ | AAK |
| 1/1 | 23.05.05 | All | Paragraphs renumbered 12, 20, 21 revised | NHJ | AAK |
| 1/2 | 30.09.05 | 1 | 22.8 added, TTRS revised | NHJ | AAK |
| 1/3 | 30.04.07 | 6 | 5 revised | NHJ | AAK |
| 1/3 | 30.04.07 | 15 | Annexure revised | NHJ | AAK |
| 1/4 | 02.06.09 | 6 | 1 revised | NHJ | AAK |
| 1/4 | 02.06.09 | 7 | 8 revised | NHJ | AAK |
| 1/4 | 02.06.09 | 9 | 15 revised | NHJ | AAK |
| 1/4 | 02.06.09 | 14 | 29 revised | NHJ | AAK |
| 1/4 | 02.06.09 | 16 | Annexure revised | NHJ | AAK |
| 3/1 | 09.10.19 | All | Reviewed | EDG | NHJ |
|  | 20.09.22 |  |  |  |  |

DESIGN STANDARD DS 26-18

Type Specifications – Electrical

Type Specification for Large Variable Speed Controllers without Input Isolating Transformers

CONTENTS

Section	Page

1	GENERAL	9

2	SITE	10

3	OPERATING MODE	10

4	AMBIENT CONDITIONS	10

5	WORK BY THE PRINCIPAL	10

6	INFORMATION TO BE PROVIDED BY THE CONTRACTOR	10

7	CONTRACTOR’S DRAWINGS	11

8	STANDARDS	11

9	QUALITY ASSURANCE	12

10	ELECTRICAL WORK	13

11	INPUT POWER SUPPLY	13

12	A.C. LINE REACTORS	13

12.1	Mounting	13

12.2	Applicable Standards	13

12.3	Audible Sound Level	13

13	SHORT CIRCUIT PROTECTION	13

14	ENCLOSURES	14

14.1	Variable Speed Controller Enclosures	14

14.2	A.C. Line Reactor Enclosures	14

15	COOLING	14

15.1	Variable Speed Controller Cooling	14

15.2	A.C. Line Reactor Cooling	14

16	LOCKING	14

17	FAULT CURRENT RATING	15

18	ARCING FAULT PROTECTION	15

19	INPUT CONVERTERS	15

19.1	Short Circuit Ratio	15

19.2	VSC Converter Type	15

19.3	Input Harmonic Currents	16

19.3.1	Basic Rectifier Type Converter	16

19.3.2	Low Harmonic Type Converters	16

19.3.3	Active Front End Type Converters	16

19.4	Input Power Factor	17

19.4.1	Basic Rectifier Type Converters	17

19.4.2	Low Harmonic Type Converters	17

19.4.3	Active Front End Type Converters	17

19.5	Ripple Filtering	17

19.6	Radio Frequency Interference	17

20	OUTPUT CONVERTERS	18

20.1	Output Inverter Type	18

20.2	Control Power	18

20.3	Output Power Supply	18

20.4	Output Ratings	18

20.5	Output Frequency Control	18

20.6	Output Voltage Control	18

20.7	Output Filtering	19

20.8	Common Mode Voltage Attenuation	19

20.9	Soft Starting	19

20.10	Ride Through Capability	20

20.11	PID Algorithm	20

21	PROTECTION AND INSTRUMENTATION	20

21.1	Protection Functions	20

21.2	Keypad and Display Unit	21

21.3	Instrumentation	21

21.4	Control and Alarm Interfaces	21

21.5	Fault Diagnostics	21

22	OVERALL EFFICIENCY	22

22.1	General	22

22.2	Basic Rectifier Converter VSC’s	22

22.3	Low Harmonic Type Converter VSC’s	22

22.4	Active Front End Type Converter VSC’s	22

23	MEAN TIME BETWEEN FAILURE	22

24	AUDIBLE SOUND LEVEL	23

25	CORROSION PROTECTION	23

26	WORKS TESTS	23

26.1	A.C. Line Reactor Type Tests	23

26.2	26.2 Separately Mounted A.C. Line Reactor Routine Tests	23

26.3	Variable Speed Controller Type Tests	23

26.4	Variable Speed Controller Routine Tests	23

26.5	Output Sinusoidal Filter Type Test	24

26.6	Output Sinusoidal Filter Routine Tests	24

26.7	Other Performance Tests	24

26.8	Test Certificates	24

27	LIQUIDATED DAMAGES FOR LOW EFFICIENCY	24

28	DELIVERY AND INSTALLATION	24

28.1	Pump Tests	24

28.2	On Site Delivery and Installation	25

29	ON SITE TESTING	25

30	AS-CONSTRUCTED INFORMATION	25

31	MANUALS	25

32	SPARE PARTS	26

33	TECHNICAL SUPPORT	26

34	TRAINING	26

35	ANNEXURE	27

36	TECHNICAL RESPONSE SCHEDULE	33

# GENERAL

This Specification covers the requirements for the design, manufacture, assembly, factory testing, delivery, on site testing and commissioning of one or more variable speed controllers without unit input isolating transformers.  The numbers required shall be as specified in the Annexure.

The scope of this Specification covers Low Voltage variable speed controller(s) with output ratings within one of the ranges listed hereunder, as specified in the Annexure.

- > 110 kW, < 450 kW at 0.415 kV

- > 220 kW, < 800 kW at 0.69 kV

Each variable speed controller shall consist of the following:

- AC line reactor (if required)

- input harmonic current filter (if required)

- input RF filter

- input power converter

- DC bus filter (if required)

- output power inverter

- common mode voltage filter or common mode voltage inductor (if required)

- sinusoidal phase to phase filter (if required)

- all other necessary filters

- cooling equipment, and

- all necessary control and protective circuitry

All of the above components shall be enclosed.

AC line reactors may be mounted separately.

All other components shall be mounted on a common base frame, as further specified hereunder.

The variable speed controllers shall be supplied to site complete and shall include all necessary accessories and miscellaneous material, minor parts and other such items to complete assembly, testing and commissioning of the variable speed controllers.

The connection of the variable speed controllers will be carried out by others after any on site assembly and positioning has been completed by the Contractor. The Contractor shall return to the site to commission the variable speed controllers once connection of the variable speed controllers is complete.

# SITE

The location of and access to the site for the installation of the variable speed controllers shall be as shown in the Annexure.

# OPERATING MODE

  - The variable speed controllers shall be suitable for controlling cage induction motors having the characteristics specified in the Annexure.

- The variable speed controllers shall be capable of operating in the mode specified in the Annexure.

# AMBIENT CONDITIONS

The variable speed controllers shall be suitable for operation at maximum load, in the specified operating mode and under the indoors ambient conditions specified in the Annexure.

# WORK BY THE PRINCIPAL

- The variable speed controller will be installed and commissioned by the Principal.

- The Principal will supply and install:

  - isolation facilities including the associated line contactor, and

  - short circuit protection of the supply to the variable speed controller in accordance with clause 13

- Other work to be undertaken by the Principal will be as specified in the Annexure.

# INFORMATION TO BE PROVIDED BY THE CONTRACTOR

The contractor shall provide the following information in respect to the variable speed controllers within the listed number of days after the receipt of the Principal’s order.

- General Arrangement Drawings	28 days

- Electrical Wiring and Schematic Drawings	28 days

- Manufacture and Delivery Schedule	14 days

- Inspection and Test Plan	35 days

- Test Certificates	On Delivery

- Operating and Maintenance Manual	On delivery

# CONTRACTOR’S DRAWINGS

The Contractor shall submit two A3 copies of the Drawings for acceptance. The drawings shall detail the general arrangement, circuit diagrams (power and control) and equipment specifications.

All drawings provided by the Contractor shall be in accordance with the latest edition of the relevant Australian Standards and shall be available in electronic format.

Adequate contrast shall be maintained between drawing detail and background, and the clarity and quality of the drawings shall enable the Principal to microfilm the prints and to reproduce by photographic processes clear and legible A3 copies for record purposes.

The drawings shall provide, in the title block, the number and the title of the Contract, as well as details to identify the drawing, its contents, revision status and date of issue.

All drawings shall be prepared using AutoCAD Release 2000 or later software. Drawings shall be prepared on A1 metric size drawing sheets, incorporating the Principal’s border and title block.

# STANDARDS

  - Unless specified otherwise, the workmanship, equipment and materials provided in accordance with this Specification shall comply in design, construction, rating and performance with the current relevant Australian or International Standards and Codes. In particular, the equipment shall comply with the requirements of AS 60146.1.

The equipment shall comply with the requirements of competent Australian Authorities having jurisdiction over all or part of the manufacture, installation and operation of the equipment.

- The equipment shall be in accordance with the requirements of AS/NZS 3000 and with the further requirements of this Specification.

- The equipment shall comply with electromagnetic interference (EMI) standards AS/NZS 61000-6-4 and AS/NZS 61000-6-2 and shall carry the CE-Mark certifying compliance with these standards.  The equipment shall be entitled to carry the Australian C-tick mark.  In addition the equipment shall comply with the further requirements of AS 61800-3.

- Each variable speed controller shall comply with the above standard when operating connected to its associated motor via motor cable of the type and length specified in the Annexure.

- Specific reference is made in this Specification to the following national and international standards.

AS 60034.1	Rotating Electrical Machines – General Requirements – Rating and Performance

AS 60146.1.1	Semiconductor converters – general requirements and line commutated converted – Specifications of basic requirements

AS 60146.1.3	Semiconductor converters – general requirements and line commutated converters – Transformers and reactors

AS 60269.4.1	Low Voltage fuses - Supplementary requirements for fuse inks for the protection of semiconductor devices

AS 60529	Degrees of protection provided by enclosures (IP Code)

AS 61800.3	Adjustable speed electrical power drive systems – EMC requirement and specific test methods

AS/NZS 61000.2.4	Compatibility levels in industrial plants for low frequency conducted disturbances

AS/NZS 61000.3.6	Assessment of emission limits for distorting loads in MV and HV power systems

AS/NZS 61000-6-2	Electromagnetic Compatibility – General Immunity Standard – Industrial Environment

AS/NZS 61000-6-4	Electromagnetic Compatibility – General Emission Standard Industrial Environment

AS/NZS 3000	Electrical Installations ‘Wiring Rules’

AS/NZS ISO 9001	Quality Management Systems – Requirements

IEC 60034.17	Rotating electrical machines – cage induction motors when fed from converters – Application guide

IEC 60721-3-3	Classification of environmental conditions - Classification of groups of environmental parameters and their severities - Stationary use at weather protected locations

AS IEC 61800-5-1	Adjustable speed electrical power drive systems
Safety requirements – electrical, thermal and energy

IEC 60034.25	Rotating electrical machines – Guidance for the design and performance of A.C. motors specifically designed for converter supply

AS/NZS 60076.6	Power Transformers – Reactors

IEEE 519	Recommended practices and requirements for harmonic control in electrical power systems

ISO 9223	Corrosion of Metals and Alloys – Classification of Corrosivity of Atmospheres

# QUALITY ASSURANCE

The variable speed controllers shall be manufactured under a Quality System certified by an Accredited Authority to be in accordance with AS/NZS ISO 9001 or an approved equivalent.

# ELECTRICAL WORK

All electrical work shall be performed by appropriately qualified and experienced personnel who shall hold a current electrical worker’s licence to perform such work. All electrical equipment shall be in accordance with any relevant clauses of AS/NZS 3000.

# INPUT POWER SUPPLY

  - The variable speed controller(s) shall be rated for operation from a 3 phase, 50 Hz (+1.5%) power supply, having a solidly grounded neutral, a RWB phase sequence and a voltage imbalance of < 3%.

  - The supply voltage and the onsite fault current level at the input terminals of the variable speed controller shall be as specified in the Annexure.

  - Provided that the VSC converter(s) comply with the harmonic current limitations specified in 19.3.1(b), 19.3.2(b) or 19.3.3(a)  [as applicable to the particular type of converter], the Principal will ensure that the design of the electrical installation into which the VSCs are to be installed is such that the voltage total harmonic distortion [THD(v)] at the input power supply to the VSC converter(s) will not exceed 10%, in accordance with AS/NZS 61000.2.4.

# A.C. LINE REACTORS

## Mounting

  - A.C. line reactors which are mounted integral with the associated converter shall be considered part of the converter and shall be specified and tested accordingly.

  - A.C. line reactors which are mounted separately shall be specified and tested separately, as hereunder.

## Applicable Standards

Separately mounted A.C. line reactors shall be air cooled reactors complying with the requirements of AS 60146.1.3 and the further requirements of AS/NZS 60076.6.

## Audible Sound Level

The audible sound power level of each A.C. line reactor, when supplying its associated variable speed controller at full load, shall not exceed 80 dBA unless a lower value is specified in the Annexure in which the latter value shall apply.

# SHORT CIRCUIT PROTECTION

  - The supply to each variable speed controller shall be from the Principal’s switchboard via a suitably rated contactor and suitably rated semiconductor protection fuses in accordance with AS 60269.4.1, all of which shall be mounted into Principal’s switchboard.

  - The ratings of such fuses shall be in accordance with the ratings specified in the Contractor’s Tender Technical Response Schedule.

# ENCLOSURES

## Variable Speed Controller Enclosures

Variable speed controller enclosures shall be floor mounted.  Variable speed controller enclosures shall be provided with a degree of protection in accordance with AS 60529 as specified in the Annexure.

## A.C. Line Reactor Enclosures

  - A.C. line reactors which are mounted integrally with the converter shall be provided with the same degree of protection as the converter.

  - Separately mounted A.C. line reactors shall be floor mounted and shall be provided with a degree of protection in accordance with AS 60529 as specified in the Annexure.

# COOLING

## Variable Speed Controller Cooling

  - For variable speed controllers, with or without integral A.C. line reactors, the primary coolant shall be air.  Each variable speed controller (including the integral A.C. line reactor if fitted) shall be force fan cooled by an integral cooling fan.

  - The secondary cooling medium shall be as specified in the Annexure.

  - If the secondary cooling medium is specified as air, the discharge cooling air shall exit near the top of each variable speed controller enclosure and facilities shall be provided to allow the discharge cooling air to be ducted directly outside the switch room building.

## A.C. Line Reactor Cooling

A.C. line reactors the primary coolant shall be air, either natural cooling or fan forced cooling by cooling fans integral to each A.C. line reactor.  The secondary medium shall be as specified in the Annexure.

# LOCKING

  - Access to all Low Voltage conductors shall be controlled by the Water Corporation standard electrical key (EL2 or bilock equivalent) of the type applicable to the particular Water Corporation Region.

  - Such access shall be controlled either by the variable speed controller doors being fitted with locks matched to the above Water Corporation key, or by providing a key interchange box between the above Water Corporation key and the variable speed controller door key.

  - In the latter case, insertion and turning the Water Corporation standard key shall release the variable speed controller door key from the key interchange box while the former shall remain trapped.

# FAULT CURRENT RATING

  - Variable speed controllers rated at 690 Volts shall have a fault current rating of not less than 30 kA

  - Variable speed controllers rated at 415 Volts shall have a fault current rating of not less than 50 kA

# ARCING FAULT PROTECTION

  - The design of the variable speed controller(s) shall be such as to minimise both the risk of an internal fault developing, and the risk of operator injury should such a fault develop.

  - Variable speed controllers shall be fitted with arcing fault detectors and associated protection relays with both solid state switch and relay outputs.

  - Arcing fault detection relays shall have normally open contacts, the rating of which shall be as shown in the Annexure.

# INPUT CONVERTERS

## Short Circuit Ratio

  - The short circuit ratio Rsc shall be defined as the ratio of the input short circuit fault current level, to the current taken by the VSC at VSC rated full load.

  - If the VSC is to be supplied via an external line reactor or line filter provided by the Contractor, the input power supply fault level shall be taken to be the fault level at the input terminals of the external line reactor or line filter. Otherwise the input power supply fault level shall be taken to be the fault level at the input terminals of the VSC proper.

## VSC Converter Type

Input converters in the variable speed controller(s) shall be one of the types listed hereunder as specified in the Annexure.

  - basic six (6) pulse rectifier type

  - low harmonic type

  - active front end type

## Input Harmonic Currents

### Basic Rectifier Type Converter

  - The internal input circuit of the VSC proper shall be an uncontrolled rectifier bridge equipped with a capacitive filter including at least either an internal 3% A.C. reactor or an internal 4% D.C. reactor.

  - With a balanced voltage test supply to the VSC proper such that Rsc = 120, the current total harmonic distortion [THD(i)] of the incoming supply current taken by the VSC shall not exceed 50% when operating at full load and without the use of external line side reactors or external harmonic filters.

  - With the on site Rsc as specified in the Annexure, the THD(i) of the incoming supply current to the VSC shall not exceed the value specified in the Annexure.

The on site incoming supply current THD(i) may be limited by external line side reactors or by external line side passive filters incorporating a ‘capacitor disconnect on falling load’ feature.

The use of external line side passive filters without a ‘capacitor disconnect on falling load’ feature shall not permitted.

  - The full load individual non-triplen odd harmonic current distortion levels taken by a basic rectifier converter from the on site input power supply specified clause 11, shall be less than the limits specified in the Contractor’s Technical Tender Response Schedule.

### Low Harmonic Type Converters

  - Low harmonic converters shall consist of basic 6 pulse converters with inbuilt active harmonic filters.

  - With a balanced voltage test supply to the VSC proper such that Rsc = 20, the total current harmonic distortion [THD(i)] of the incoming supply current taken by the VSC shall not exceed 5% when operating at full load.

In addition the odd harmonic current levels shall not exceed those specified in Table 10.3, IEEE 519 for a value of Rsc of < 20.

  - Regardless of the value of the onsite Rsc, at full load the total current harmonic distortion [THD(i)] of the incoming supply current taken by the VSC, from the site power supply, shall not exceed 8 % and the odd harmonic current levels shall not be more than 50 % greater than the values specified in Table 10.3, IEEE 519 for a value of Rsc < 20.

### Active Front End Type Converters

  - With a balanced voltage test supply to the VSC proper such that Rsc = 20, the current total harmonic distortion [THD(i)] of the incoming supply current taken by the VSC shall not exceed 5% when operating at full load.

In addition the odd harmonic current levels shall not exceed those specified in Table 10.3, IEEE 519 for a value of Rsc of < 20.

- Regardless of the value of the onsite Rsc, at full load the total current harmonic distortion [THD(i)] of the incoming supply current taken by the VSC, from the site power supply, shall not exceed 8 % and the odd harmonic current levels shall not be more than 50 % greater than the values specified in Table 10.3, IEEE 519 for a value of Rsc < 20.

## Input Power Factor

### Basic Rectifier Type Converters

  - With a balanced voltage test supply to the VSC proper such that Rsc = 120, the displacement power factor of the input current taken by each converter shall not be less than 0.95 over an input current range of 50% to 100% of full load current.

- If the converter input current is reduced to 30% full load current, the input displacement power factor shall not fall to less than 0.80.

### Low Harmonic Type Converters

With a balanced voltage test supply to the VSC proper such that      Rsc = 20, the displacement power factor of the input current taken by each converter shall not be less than 0.90 over an input current range of 30% to 100% of full load current.

### Active Front End Type Converters

With a balanced voltage test supply to the VSC proper such that     Rsc = 20, the displacement power factor of the input current taken by each converter shall be settable over a range of 0.8 leading to 0.8 lagging, and shall be constant at the set point, over an input current range of 30% to 100% of full load current.

## Ripple Filtering

Variable speed controllers having input converters of the sinusoidal rectifier type shall be fitted with input ripple filters which shall be tuned to the modulating frequency and its low order harmonics so as to prevent modulating ripple in the input voltage wave form.

## Radio Frequency Interference

  - Variable speed controllers rated < 220 kW, when installed and connected to their associated motors by the lengths and types of cable specified in the Annexure, shall not cause radio frequency interference greater than the limits specified in AS/NZS 61800.3 for Category C3 equipment.

- Variable speed controllers rated > 220 kW, when installed and connected to their associated motors by the lengths and types of cable specified in the Annexure, shall not cause radio frequency interference greater than the limits specified in AS/NZS 61800.3 for Category C4 equipment.

# OUTPUT CONVERTERS

## Output Inverter Type

Output inverters shall be pulse width modulated (PWM) type and shall be voltage source type or current source type.

## Control Power

  - If a variable speed controller’s control power is not provided internally, control power will be provided by the Principal.

- If the latter is the case, the variable speed controller shall be designed to operate from a 3 phase, 4 wire, 415 Volt +/- 10% control power supply.

## Output Power Supply

  - Each variable speed controller shall provide a 3 phase power supply output having an RWB phase sequence and a controlled frequency range as specified in the Annexure.

- The output power supply shall be suitable for driving the associated motor and its associated load, all as specified in the Annexure.

## Output Ratings

  - Each variable speed controller shall have output kVA ratings at minimum 30Hz frequency and at 50 Hz as specified in the Annexure

- The output current rating shall be constant over the frequency range specified in the Annexure

- Each variable speed controller shall have a short time (10 second) over current capacity as specified in the Annexure

## Output Frequency Control

  - The static frequency control error over the specified frequency range shall be not greater than 1% nominal frequency

  - Variable speed controllers shall include facilities to enable driven load resonant frequencies to be bypassed

## Output Voltage Control

  - Variable speed controller output voltage at motor rated frequency shall be the motor rated voltage as specified in the Annexure.

Generally, the output voltage shall be varied in direct proportion to the output frequency.

- However the inverter control algorithm shall incorporate an energy saver facility which shall adjust the output voltage as a function of load so as to provide maximum motor efficiency.

- Notwithstanding the above, at frequencies above the motor rated frequency the output voltage shall be limited to the motor rated voltage.

## Output Filtering

- Low Voltage variable speed controller(s) shall be fitted with output sinusoidal Type 1 filters (symmetric plus asymmetric) providing both phase to phase and phase to earth filtering if any of the following are specified in the Annexure to apply:

- the length of the motor cable exceeds 150 metres

- the associated motors are submersible borehole motors

- If the variable speed controller is specified in the Annexure to be suitable for controlling a conventional Low Voltage cage motor with a motor cable length less than 150 metres, the variable speed controller(s) shall be fitted with dV/dt filters so as to limit the impulse voltage levels to less than the limits specified in Figure 17 of IEC 60034.17

## Common Mode Voltage Attenuation

  - If the motors to be controlled by the variable speed controller(s) are specified in the Annexure to be provided with insulated drive end and non-drive end bearings, shaft grounding ring(s) and insulated drive coupling(s) or fitted with Type 1 sinusoidal filters as per clause 20.7 (a) above, the variable speed controller(s) need not be fitted with common mode voltage attenuation. Otherwise variable speed controller(s) shall be fitted with common mode voltage attenuation as hereunder.

  - Except as specified clause 20.8 (a) above, common mode voltage attenuation shall be incorporated into the variable speed controller(s) and shall be provided by one of the following means:

- conventional common mode voltage filters,

- wound ferrite core common mode inductors,

- feed through ferrite core common mode inductors in conjunction with dV/dt filters.

## Soft Starting

  - Variable speed controllers shall include a soft starting facility which shall provide the motor with a starting sequence which ensures that the motor does not draw more than 110% of full load current during the starting period.

- The type of driven load shall be as specified in the Annexure.

- Assuming standard cage induction motors, the variable speed controllers shall be capable of providing a starting torque margin of not less than 10 % over the driven load starting torque requirement.

- The starting period shall be adjustable over a range of not less than 5 seconds to 2000 seconds.

## Ride Through Capability

Each variable speed controller shall incorporate control algorithms which allow the controller to:

  - stay on line at reduced load in the event of controller over temperature

  - stay on line at reduced load in the event of continuous input under voltage not more than -15 %

  - stay on line at reduced load in the event of continuous input over voltage not more than +10%

  - ride through a 0.5 second input power voltage dip of up to 30 %

  - ride through a loss of input power of up to 2 cycles

## PID Algorithm

Each variable speed controller shall be equipped with a PID control algorithm so as to allow the control of process variables such as pressure, flow or fluid level via control of the driven motor speed. The required input signal to the control algorithm shall be a 4/20 mA analogue current signal.

# PROTECTION AND INSTRUMENTATION

## Protection Functions

Variable speed controllers shall incorporate the following protection functions:

- A.C. input or D.C. bus over voltage

- A.C. input or D.C. bus under voltage

- input phase loss

- output phase loss

- controller over temperature

- output over current

- output earth fault (if output neutral is solidly grounded)

- output neutral displacement (if output neutral is not solidly grounded)

- motor overload

- backspinning start protection (if so, required in the Annexure)

- stall protection (if so, required in the Annexure)

- other protection functions as specified in the Annexure

## Keypad and Display Unit

Each variable speed controller shall be equipped with a keypad and display unit providing status indication, fault indication, and allowing control and parameter settings and adjustments.

## Instrumentation

Each variable speed controller shall be equipped with instrumentation to provide a read out of the following parameters:

  - output voltage

  - output current

  - output frequency

  - output power (kW)

  - output energy (kWHr)

## Control and Alarm Interfaces

Each variable speed controller shall be able to be equipped with the following control and alarm interfaces and shall be supplied with interfaces selected and assigned as specified in the Annexure:

- Modicon Modbus bus interface

- Profibus bus interface

- Ethernet bus interface

- Two (2) programmable isolated 4/20 mA inputs

- Two (2) programmable isolated digital inputs

- Two (2) programmable isolated 4/20 mA outputs

- Three (3) programmable isolated digital outputs

- One (1) programmable non isolated potentiometer input

## Fault Diagnostics

Each variable speed controller shall be equipped with a full suite of diagnostic software tools to facilitate commissioning and fault finding.

# OVERALL EFFICIENCY

## General

  - The variable speed controller’s efficiency shall be defined as the ratio of the power supplied to the motor to the power provided to the input terminals of the overall variable speed controller, expressed as a percentage.

  - Consequently the variable speed controller’s efficiency shall take into account losses in input devices (such as A.C. line reactors, input harmonic filters) and output devices (such as sine filters), as well as losses in the variable speed controller proper.

## Basic Rectifier Converter VSC’s

- With a balanced voltage test supply to each VSC proper such that Rsc = 120, the overall efficiency of each 6 pulse rectifier converter VSC, without an output filter, shall be > 98% at 50 Hz and 100% load, and shall be > 95% at 38 Hz and 45% full load.

- With a balanced voltage test supply to each VSC proper such that Rsc = 120, the overall efficiency of each 6 pulse rectifier converter VSC with an output filter, shall be > 97% at 50 Hz and 100% load, and shall be > 94% at 38 Hz and 45% full load.

## Low Harmonic Type Converter VSC’s

- With a balanced voltage test supply to each VSC proper such that Rsc = 20, the overall efficiency of each low harmonic variable speed controller, without output filter, shall be > 96% at 50 Hz and 100% load, and shall be > 93% at 38 Hz and 45% full load.

- With a balanced voltage test supply to each VSC proper such that Rsc = 20, the overall efficiency of each low harmonic variable speed controller, with output sinusoidal filter or with dV/dt output filter, shall be > 95% at 50 Hz and 100% load, and shall be > 92% at 38 Hz and 45% full load.

## Active Front End Type Converter VSC’s

- With a balanced voltage test supply to each VSC proper such that Rsc = 20, the overall efficiency of each active front end variable speed controller, without output filter, shall be > 98% at 50 Hz and 100% load, and shall be > 95% at 35 Hz and 30% full load.

- With a balanced voltage test supply to each VSC proper such that Rsc = 20, the overall efficiency of each Low Voltage active front end variable speed controller, with sinusoidal output filter or with dV/dt output filter, shall be > 97% at 50 Hz and 100% load, and shall be > 94% at 35 Hz and 30% full load.

# MEAN TIME BETWEEN FAILURE

Variable speed controllers shall have a Mean Time Between Failure rating of not less than 50,000 operating hours.

# AUDIBLE SOUND LEVEL

At full load the sound power level of each variable speed converter (including the A.C. line reactor if the latter is integral with the controller) shall not be more 93 dBA (i.e. the sound pressure level at 1 metre shall not be more than 85 dBA), unless a lower value is specified in the Annexure in which case the latter shall apply.

# CORROSION PROTECTION

  - All metallic parts shall be provided with appropriate corrosion protection by metallic plating or by paint finishes.

  - Outside steel surfaces of the variable speed controller enclosure shall with medium term protection to category 3 in accordance with ISO 9223 (industrial and marine environments), either by gloss paint or by powder coating finish.

  - Outside aluminum surfaces of the variable speed controller enclosure shall be protected by anodic oxide coatings with a minimum average coating thickness of 25 microns and a minimum local coating thickness of 20 microns.

  - The variable speed controller(s) shall be supplied with high grade conformal coated electronics to ensure the drives are suitable for installation in harsher environments as classified by IEC 60721-3-3, Class 3C3.

# WORKS TESTS

## A.C. Line Reactor Type Tests

A.C. line reactors shall be type tested in accordance with Section 8.9.3 Type Tests of AS/NZS 60076.6.

## Separately Mounted A.C. Line Reactor Routine Tests

Separately mounted A.C. line reactors shall be routine tested in accordance with Section 8.9.2 Routine Tests of AS/NZS 60076.6.

## Variable Speed Controller Type Tests

- The variable speed controller including its control, protection and auxiliary sections shall be type tested in accordance with AS 60146.1.1.

- In addition the variable speed controller shall be impulse voltage type tested in accordance with AS IEC 61800-5-1

## Variable Speed Controller Routine Tests

The variable speed controller including its control, protection and auxiliary section shall be routine tested in accordance with AS 60146.1.1.

## Output Sinusoidal Filter Type Test

If a sinusoidal filter is to be provided, it shall be of a type tested design in accordance with the requirements of AS 60146.1.3.

## Output Sinusoidal Filter Routine Tests

If a sinusoidal filter is to be provided, it shall be routine tested in accordance with the requirements of AS 60146.1.3.

## Other Performance Tests

The converter shall be submitted to testing in order to substantiate all of the other performance values included on the Contractor’s tender.

## Test Certificates

Type test and routine test certificates certifying successful completion of such tests shall be presented to the Principal prior to the equipment leaving the equipment manufacturer’s works and equipment shall not leave the manufacturer’s works until the Principal has accepted in writing that the test certificates are in accordance with the Contract.

# LIQUIDATED DAMAGES FOR LOW EFFICIENCY

In addition to any damages specified in the General Conditions of Contract, the Contractor shall be liable to the Principal for liquidated damages in respect to failure of the variable speed controller to achieve the level of full speed efficiency quoted previously in the Tender Response Schedule.  Such liquidated damages shall be calculated on the basis of the capitalised cost of losses quoted in the Annexure and by the amount by which the full load full speed efficiency falls short of 99% of the quoted full load speed efficiency.

# DELIVERY AND INSTALLATION

## Pump Tests

If so specified in the Annexure the Contractor shall deliver one complete variable speed controller to the pump manufacturer’ works specified in the Annexure, so as to facilitate pump acceptance tests.

In such cases, the Contractor shall deliver to, and unload unpack and assemble as necessary the complete variable speed controller at the pump manufacturer’s works.

The Contractor shall supervise the connection and operation of the variable speed controller during pump testing.

Once pump testing is complete, the Contractor shall dissemble (to the extent necessary) the variable speed controller and pack, load and deliver the complete variable speed controller to the site as specified hereunder.

## On Site Delivery and Installation

The Contractor shall deliver to, and unload, unpack and assemble as necessary the complete variable speed controllers at the site.

The Contractor shall inspect all of the unpacked variable speed controllers and shall ensure that the variable speed controllers are undamaged.

The Contractor shall give the Principal seven days notice when the variable speed controllers will be ready for installation. The Contractor shall install the variable speed controllers in their permanent positions ready for connection by others.

# ON SITE TESTING

Before the Contractor makes each variable speed controller available to the Principal for connection to the electrical system, the Contractor shall carry out an insulation resistance test on each variable speed controller including its A.C. line reactor if applicable.

Once each variable speed drive has been connected, the Contractor shall commission each variable speed controller in association with the Principal.

Each variable speed controller shall be operated on load for a minimum period of 3 hours during which time the Contractor shall monitor its operation.

The Contractor shall supply all equipment, materials and labour for such testing and commissioning of the variable speed controller.

The Contractor shall make the results of commissioning tests available to the Principal within 7 days of the completion of such tests.

# AS-CONSTRUCTED INFORMATION

The Contractor shall provide as-constructed information on all drawings.

As-constructed drawings shall be provided in an electronic form with A3 size hard copies.

# MANUALS

The Contractor shall supply 3 copies of comprehensive instruction manuals, written in English and covering the complete operation and maintenance requirements of all equipment supplied under the Contract.

The manuals shall be printed on high grade A4 size paper and shall be bound in a high grade A4 size loose leaf binder.

Information included in the manuals shall include:

- operating instructions

- safety instructions and warnings

- maintenance instructions and schedules

- recommended spare parts and special tool list

- as constructed drawings

- detailed equipment performance specifications, and

- test reports and test certificates

# SPARE PARTS

The Contractor shall supply as a minimum, one complete set of power electronics modules.

The Contractor shall guarantee to hold in Australia, one complete set of electronics spare parts for one variable speed controller.

# TECHNICAL SUPPORT

The Contractor shall maintain an adequate level of technical support within Australia.

# TRAINING

The Contractor shall supply, as part of the Contract, training for the number of Water Corporation electrical technicians specified in the Annexure. Such training shall cover commissioning as well as first line fault finding and first line servicing.

# ANNEXURE

Annexure to Specification

for

Large Variable Speed Controller(s) without Input Isolating Transformer(s)

Project:

Titles of Driven Loads

Number of VSC’s required (clause 1 refers)

Site Location (clause 2 refers)

Access to Site (clause 2 refers)

Operating Mode

Input Power Supply (clause 11 refers)

Supply Voltage 	 kV

Short Circuit Current Level 	kA

Motor Characteristics (clauses 3, 20.3, 20.6, 20.7 refer)

Type of Motor (i.e. conventional or bore hole submersible)

Motor(s) fitted with insulated DE and NDE bearings, grounding

rings and insulated drive couplings (yes or no)

Type of Duty as per AS 60034.1

Rated Voltage (phase to phase) 	 Volts

Rated Current  	 Amps

Rated Frequency 	 Hz

Rated Speed 	 rpm

Rated Output as Rated Speed 	 kW

Variable Speed Controller Characteristics (clauses 3, 19.1, 20.3, 20.7 refers)

Required Type of Converter

Required kVA at Minimum Specified Output Frequency 	 kVA

Required Output Operating Frequency Range 	 Hz to 	Hz

Required kVA at Maximum Specified Output Frequency 	 kVA

Required Output Voltage at Specified Maximum Output Frequency  	...Volts

THD(i) of the incoming supply current to VSC (Clause 19.3.1 refers)…………………at RSC of…….

Additional Harmonic limit requirements (If required)…………………………………………………

………………………………………………………………………………………………………….

Required Power Factor Setting (for AFE VSC’s only)

Required Output 10 Second Over Current Capacity 	% VSC Rated Current

Load Characteristics (clauses 3, 20.3, 20.9 refer)

Title of Driven Load

Type of Load (e.g. centrifugal water pump)

Load at Minimum Frequency 	 kW

Load Torque versus Speed Characteristics:

Newton*m at	 0 rpm		Newton*m at	rpm

Newton*m at 	rpm			Newton*m at	rpm

Ambient Conditions (clause 4 refers)

Variable Speed Controllers

Maximum Ambient air Temperature 	 oC

Minimum Ambient Air Temperature 	 oC

Maximum Ambient Air Humidity 	%

Ambient Airborne Contaminants

Separately Mounted A.C. Line Reactors (if applicable)

Maximum Ambient air Temperature 	 oC

Minimum Ambient Air Temperature 	 oC

Maximum Ambient Air Humidity 	%

Ambient Airborne Contaminants

Work by the Principal (clause 5 refers)

Annexure to Specification

for

Large Variable Speed Controller(s) without Input Isolating Transformer(s)

Type of Motor Feed Cable (clauses 8, 20.7 refer)

Length of Motor Feed Cable (clause 8 refers)

Enclosures (clause 14 refers)

Variable Speed Controller Enclosures

Protection Class as per AS 60529 	IP

Cable Connection (i.e. top or bottom entry)

Front Access Only (required or not required)

Separately Mounted A.C. Line Reactors

Separate Mounting (permitted or not permitted)

Protection Class as Per AS 60529 	IP

Cable Connection (i.e. top or bottom entry)

Front Access Only (required or not required)

Cooling (clause 15 refers)

Variable Speed Controller Cooling

Type of Secondary Coolant (i.e. air or water)

Separately Mounted A.C. Line Reactor Cooling

Type of Secondary Coolant (i.e. air or water)

Range of coolant temperature at motor inlet 	oC to 	oC

Sodium 	mg/1	Potassium 	mg/1

Magnesium 	mg/1	Calcium 	mg/1

Bicarbonate 	mg/1	Sulphate 	mg/1

Chloride 	mg/1	Nitrate 	mg/1

Carbonate 	mg/1	Silica 	mg/1

Total soluble salts 	mg/1	Iron 	mg/1

Total hardness	mg/1

Alkalinity (as Ca Co3) 	mg/1		pH

Arcing Fault Protection (clause 18 refers)

Arcing Fault Detection.  Relay Output Contacts Ratings:  AC or DC

Volts		Amps

Annexure to Specification

for

Large Variable Speed Controller(s) without Input Isolating Transformer(s)

Inverter Output Ratings (clause 20.4 refers)

Output rating kW at 50Hz output frequency 	kW

Output rating kW at minimum output frequency 	kW

10 seconds overcurrent capacity 	Amps

Protection and Instrumentation (clause 21.1 refers) 	
Back Spin Protection (required or not required)

Stall Protection (required or not required)

Other Protection Functions required

Control and Alarm Interfaces (clause 21.4 refers)

Required Types of Control and Alarm interfaces

Audible Sound Level (clause 24 refers)

Variable Speed Controller Sound Level

Maximum Full Load Sound Power Level (if <93 dBA)	 dBA

Separately Mounted A.C. Line Reactor Sound Level

Maximum Full Load Sound Power Level (if < 93 dBA) 	dBA

Liquidated Damages for Low Efficiency (clause 27 refers)

Capitalised Cost of Losses 	$/kW

Pump Tests

Tests at Pump Manufacturer’s Works (required or not required)

Address of Pump Manufacturer’s Works

Training

Number of Technician Training Places Required

# TECHNICAL RESPONSE SCHEDULE

| Type Specification for Large Variable Speed Controllers without Input Isolating Transformers Tender Response Schedule |
| --- |
| DS 26.18 | Subject | Noted | Compliance | Comments |
| Clause No. |  |  | Yes | No |  |
| 1. | General |  |  |  |  |
| 2. | Site |  |  |  |  |
| 3. | Operating Mode |  |  |  |  |
| 4. | Ambient Conditions |  |  |  |  |
| 5. | Work by Principal |  |  |  |  |
| 6. | Information from Contractor |  |  |  |  |
| 7. | Contractor’s Drawings |  |  |  |  |
| 8. | Standards |  |  |  |  |
| 9. | Quality Assurance |  |  |  |  |
| 10. | Electrical Work |  |  |  |  |
| 11. | Input Power Supply |  |  |  | Frequency tolerance % = |
|  |  |  |  |  | Voltage tolerance % = |
| 12. | A.C. Line Reactors |  |  |  |  |
| 12.1 | Mounting |  |  |  | Integral or separate |
| 12.2 | Applicable Standards |  |  |  |  |
| 12.3 | Audible Sound Level |  |  |  | dBA = |
| 13. | Short Circuit Protection |  |  |  | If fuse, fuse rated amps = |
|  |  |  |  |  | If ACB, full load setting amps = |
| 14. | Enclosure |  |  |  | DMTD amps = at ms |
| 14.1 | VSC Enclosures |  |  |  | Wall or floor mounted ? |
|  |  |  |  |  | IP = |
| 14.2 | A.C. Line Reactor Enclosure |  |  |  | IP = |
| 15. | Cooling |  |  |  |  |
| 15.1 | VSC Cooling |  |  |  |  |
|  | If air cooled |  |  |  | Cooling air flow rate, litres/sec = |
|  |  |  |  |  | Allowable duct head loss, mm Hg = |
|  | If water cooled |  |  |  | Cooling water flow rate, litres/sec |
| 15.2 | A.C. Line Reactor Cooling |  |  |  | Natural or fan cooled? |
|  | If fan cooled |  |  |  | Air flow rate, litres/sec = |
|  |  |  |  |  | Allowable duct head loss, mm Hg = |
| 16. | Locking |  |  |  |  |
| 17. | Fault Current Rating |  |  |  | Fault kA rating = |
| 18. | Arcing Fault Protection |  |  |  | Fuse I2t, Amp2sec = Arc detectors fitted? |
| 19. | Input Converters |  |  |  |  |
| 19.1 | Short Circuit Ratio |  |  |  | Rsc % = |
| 19.2 | VSC Converter Type |  |  |  | Converter type = |
|  |  |  |  |  | No. pulses = |
| 19.3 | Input Harmonic Currents |  |  |  | With test Rsc = |
|  |  |  |  |  | full load THD(i) = |
|  |  |  |  |  | With at site Rsc = |
|  |  |  |  |  | full load THD(i) = |
|  |  |  |  |  | Full load max. Ih% for listed values of h |
|  |  |  |  |  | h ≤ 11 = 11 >h ≤ 17 = 17 >h ≤ 23 = 23 > h ≤ 35 = 35 > h ≤ 49 = |
| 19.4 | Input Power Factor |  |  |  | P.F. at 100% rated current = P.F. at 30% rated current = |
| 19.5 | Ripple Filtering |  |  |  |  |
| 19.6 | Radio Frequency Interference |  |  |  | AS/NZS 61800.0 Category = |
| 20. | Output Convertors |  |  |  |  |
| 20.1 | Output Inverter Type |  |  |  |  |
| 20.2 | Control Power |  |  |  |  |
|  | If not internal |  |  |  | kVA = |
|  |  |  |  |  | Volts = |
|  |  |  |  |  | No phases = |
| 20.3 | Output Power Supply |  |  |  | Maximum frequency, Hz = |
|  |  |  |  |  | Minimum frequency, Hz = |
| 20.4 | Output Ratings |  |  |  | 60 Hz Rated kVA = |
|  |  |  |  |  | 10 sec. O/C Amps = |
| 20.5 | Output Frequency Control |  |  |  | Max. control error % = |
| 20.6 | Output Voltage Control |  |  |  | At maximum frequency kV = |
| 20.7 | Output Filtering |  |  |  | Sinusoidal filters or dV/dt filters provided? |
| 20.8 | Common Mode Voltage Attenuation |  |  |  | If provided, type (i) (ii) or (iii) |
|  |  |  |  |  | Attenuation as per sub-clause (b)? |
| 20.9 | Soft Starting |  |  |  | Starting current limit, % = |
| 20.10 | Ride Through Capability |  |  |  | At 85% volts, output kVA = |
|  |  |  |  |  | At 110% volts, output kVA = |
|  |  |  |  |  | Max. Ride through volts dip. % = |
|  |  |  |  |  | Max. ride through time, cycles = |
| 20.11 | PID Algorithm |  |  |  |  |
| 21. | Protection and Instrumentation |  |  |  |  |
| 21.1 | Protection Functions |  |  |  | Attach details separately |
| 21.2 | Keypad and Display Unit |  |  |  |  |
| 21.3 | Instrumentation |  |  |  |  |
| 21.4 | Control and Alarm Interfaces |  |  |  | Attach details separately |
| 21.5 | Fault Diagnostics |  |  |  | Attach details separately |
| 22. | Overall Efficiency |  |  |  |  |
| 22.1 | General |  |  |  |  |
| 22.2 | Basic Rectifier VSC Overall efficiency at Rsc = 120 w/o output filter w/o output filter w/- sine output filter w/- sine output filter w/- dV/dt output filter w/- dV/dt output filter |  |  |  | ( at 100% rated amps and 50 Hz = ( at 45% rated amps and 38 Hz = ( at 100% rated amps and 50 Hz = ( at 45% rated amps and 38 Hz = ( at 100% rated amps and 50 Hz = ( at 45% rated amps and 38 Hz = |
| 22.3 | Low Harmonic Converter VSCs Overall Efficiency at Rsc = 20 w/o output filter w/o output filter w/- sine output filter w/- sine output filter w/- dV/dt output filter w/- dV/dt output filter |  |  |  | ( at 100% rated amps and 50 Hz = ( at 45% rated amps and 38 Hz = ( at 100% rated amps and 50 Hz = ( at 45% rated amps and 38 Hz = ( at 100% rated amps and 50 Hz = ( at 45% rated amps and 38 Hz = |
| 22.4 | AFE Converter VSCs Overall Efficiency at Rsc = 20 w/o output filter w/o output filter w/- sine output filter w/- sine output filter w/- dV/dt output filter w/- dV/dt output filter |  |  |  | ( at 100% rated amps and 50 Hz = ( at 30% rated amps and 35 Hz = ( at 100% rated amps and 50 Hz = ( at 30% rated amps and 35 Hz = ( at 100% rated amps and 50 Hz = ( at 30% rated amps and 35 Hz = |
| 23. | Mean Time Between Failure |  |  |  | MTBF, hours = |
| 24. | Audible Sound Power Level |  |  |  | VSC Sound Power, dBA = |
|  |  |  |  |  | VSC Sound Pressure @ 1m, dBA |
|  |  |  |  |  | Tfr. Sound Power, dBA = |
| 25. | Corrosion Protection |  |  |  | High grade conformal coated electronics 3C3 = Yes/No |
| 26. | Works Tests |  |  |  |  |
| 26.1 | A.C. Line Reactor Type Tests |  |  |  |  |
| 26.2 | Separately Mounted A.C. Line Reactor Routine Tests |  |  |  |  |
| 26.3 | VSC Type Tests |  |  |  |  |
| 26.4 | VSC Routine Tests |  |  |  |  |
| 26.5 | Output Sinusoidal Filter Type Tests |  |  |  |  |
| 26.6 | Output Sinusoidal Filter Routine Tests |  |  |  |  |
| 26.7 | Other Performance Tests |  |  |  |  |
| 26.8 | Test Certificates |  |  |  |  |
| 27. | Liquidated Damages for Low Efficiency |  |  |  |  |
| 28. | Delivery and Installation |  |  |  |  |
| 28.1 | Pump Tests |  |  |  |  |
| 28.2 | On Site Delivery and Installation |  |  |  |  |
| 29. | On Site Testing |  |  |  |  |
| 30. | As Constructed Information |  |  |  |  |
| 31. | Manuals |  |  |  |  |
| 32. | Spare Parts |  |  |  |  |
| 33. | Technical Support |  |  |  | Technical support function location is located in |
| 34. | Training |  |  |  |  |

END OF DOCUMENT