Assets Planning and Delivery Group Engineering

DESIGN STANDARD DS 26-28

Type Specifications – Electrical

Type Specification for Ground Mounted Oil Filled Transformers

version 2 revision 2

June 2022

FOREWORD

The intent of Design Standards is to specify requirements that assure effective design and delivery of fit for purpose Water Corporation infrastructure assets for best whole-of-life value with least risk to Corporation service standards and safety. Design standards are also intended to promote uniformity of approach by asset designers, drafters and constructors to the design, construction, commissioning and delivery of water infrastructure and to the compatibility of new infrastructure with existing like infrastructure.

Design Standards draw on the asset design, management and field operational experience gained and documented by the Corporation and by the water industry generally over time. They are intended for application by Corporation staff, designers, constructors and land developers to the planning, design, construction and commissioning of Corporation infrastructure including water services provided by land developers for takeover by the Corporation.

Nothing in this Design Standard diminishes the responsibility of designers and constructors for applying the requirements of the Western Australia's Work Health and Safety (General) Regulations 2022 to the delivery of Corporation assets. Information on these statutory requirements may be viewed at the following web site location:

Overview of Western Australia’s Work Health and Safety (General) Regulations 2022 (dmirs.wa.gov.au)

Enquiries relating to the technical content of a Design Standard should be directed to the Senior Principal Engineer - Electrical, Engineering. Future Design Standard changes, if any, will be issued to registered Design Standard users as and when published.

Head of Engineering

This document is prepared without the assumption of a duty of care by the Water Corporation.  The document is not intended to be nor should it be relied on as a substitute for professional engineering design expertise or any other professional advice.

It is the responsibility of the user to ensure they are using the current version of this document.

© Copyright – Water Corporation: This standard and software is copyright.  With the exception of use permitted by the Copyright Act 1968, no part may be reproduced without the written permission of the Water Corporation.

DISCLAIMER

Water Corporation accepts no liability for any loss or damage that arises from anything in the Standards/Specifications including any loss or damage that may arise due to the errors and omissions of any person. Any person or entity which relies upon the Standards/Specifications from the Water Corporation website does so that their own risk and without any right of recourse to the Water Corporation, including, but not limited to, using the Standards/Specification for works other than for or on behalf of the Water Corporation.

The Water Corporation shall not be responsible, nor liable, to any person or entity for any loss or damage suffered as a consequence of the unlawful use of, or reference to, the Standards/Specifications, including but not limited to the use of any part of the Standards/Specification without first obtaining prior express written permission from the CEO of the Water Corporation.

Any interpretation of anything in the Standards/Specifications that deviates from specific Water Corporation Project requirements must be referred to, and resolved by, reference to and for determination by the Water Corporation’s project manager and/or designer for that particular Project.

REVISION STATUS

The revision status of this standard is shown section by section below. It is important to note that the latest revisions including additions, deletions and changes to this version of the standard are also identified by the use of a vertical line in the left hand margin, adjacent to the revised section.

| REVISION STATUS |
| --- |
| SECT. | VER./REV | DATE | PAGES REVISED | REVISION DESCRIPTION (Section, Clause, Sub-Clause) | RVWD. | APRV. |
| 1 | 2/0 | 14.01.16 | 8 | Revised | NJ | MSP |
| 1 | 2/1 | 07.08.19 | 8 | Revised | EDG | NHJ |
| 5 | 2/0 | 14.01.16 | 8-9 | Revised | NJ | MSP |
| 5 | 2/1 | 07.08.19 | 8-9 | Revised | EDG | NHJ |

| 6 | 2/0 | 14.01.16 | 9 | Revised | NJ | MSP |
| --- | --- | --- | --- | --- | --- | --- |
| 6 | 2/1 | 07.08.19 | 9 | Revised | EDG | NHJ |

| 9 | 2/0 | 14.01.16 | 10 | Revised | NJ | MSP |
| --- | --- | --- | --- | --- | --- | --- |
| 9 | 2/1 | 07.08.19 | 10 | Revised | EDG | NHJ |

| 10 | 2/0 | 14.01.16 | 10 | Revised | NJ | MSP |
| --- | --- | --- | --- | --- | --- | --- |

| 11 | 2/0 | 14.01.16 | 10 | Revised | NJ | MSP |
| --- | --- | --- | --- | --- | --- | --- |
| 11 | 2/1 | 07.08.19 | 10 | Revised | EDG | NHJ |

| 12 | 2/0 | 14.01.16 | 10-14 | New and revised | NJ | MSP |
| --- | --- | --- | --- | --- | --- | --- |
| 12 | 2/1 | 07.08.19 | 10-16 | 12.2, 12.7, 12.9, 12.10, 12.11.2, 12.11.4 revised | EDG | NHJ |

| 13 | 2/0 | 14.01.16 | 16 | Revised | NJ | MSP |
| --- | --- | --- | --- | --- | --- | --- |
| 13 | 2/1 | 07.08.19 | 16 | Revised | EDG | NHJ |

| 14 | 2/0 | 14.01.16 | 16-17 | Revised | NJ | MSP |
| --- | --- | --- | --- | --- | --- | --- |
| 14 | 2/1 | 07.08.19 | 16-17 | 14.3, 14.4, 14.5 revised | EDG | NHJ |

| 16 | 2/0 | 14.01.16 | 17 | Revised | NJ | MSP |
| --- | --- | --- | --- | --- | --- | --- |
| 16 | 2/1 | 07.08.19 | 17 | Revised | EDG | NJH |

| 17 | 2/0 | 14.01.16 | 18 | Revised | NJ | MSP |
| --- | --- | --- | --- | --- | --- | --- |

| PREVIOUS REVISION STATUS |
| --- |
| VER./ REV. | DATE | PAGES REVISED | REVISION DESCRIPTION (Section, Clause, Sub-Clause) | RVWD. | APRV. |
| 1/0 | 30.09.04 | All | New Version | NHJ | AAK |
| 1/1 | 23.05.05 | All | Paragraphs Renumbered | NHJ | AAK |
| 1/2 | 02.06.09 | 6 | 1 revised | NHJ | AAK |
| 1/2 | 02.06.09 | 7 | 6 revised | NHJ | AAK |
| 1/2 | 02.06.09 | 8 | 12.1 revised | NHJ | AAK |
| 1/2 | 02.06.09 | 9 | 12.2 revised | NHJ | AAK |
| 1/2 | 02.06.09 | 11 | 13.1, 13.2 revised | NHJ | AAK |
| 1/2 | 02.06.09 | 12 | 16.3 revised | NHJ | AAK |
| 1/2 | 02.06.09 | 13, 14, 17 | Annexure revised | NHJ | AAK |
| 2/1 | 07.08.19 | 19-27 | Annexure revised | EDG | NHJ |
| 2/2 | 14.06.22 | All | Document reviewed and no change required | EDG | EDG |

DESIGN STANDARD DS 26-28

Type Specifications – Electrical

Type Specification for Ground Mounted Oil Filled Transformers

CONTENTS

Section	Page

1	GENERAL	8

2	SITE	8

3	WORK BY THE PRINCIPAL	8

4	INFORMATION TO BE PROVIDED BY THE CONTRACTOR	8

5	CONTRACTOR’S DRAWINGS	8

6	STANDARDS	9

7	QUALITY ASSURANCE	9

8	SAFETY REQUIREMENTS – ELECTRICAL WORK	10

9	POWER SUPPLY	10

10	OPERATING MODE	10

11	SITE AMBIENT CONDITIONS	10

12	TECHNICAL REQUIREMENTS	10

12.1	Standards	10

12.2	Linear Load kVA Rating	10

12.3	Non-linear Load Output Current Rating	10

12.4	Types of Load Losses	11

12.5	Load Harmonic Profile Factors	11

12.5.1	General	11

12.5.2	RMS Current Loss Factor	11

12.5.3	Eddy Current Loss Factor	11

12.5.4	Other Stray Loss Factor	11

12.5.5	Calculation of Load Losses	12

12.6	Functional Requirements	12

12.7	Transformer Service Conditions	13

12.8	Design	13

12.9	Performance Requirements	13

12.10	Miscellaneous Fittings	14

12.11	Construction Requirements	14

12.11.1	General	14

12.11.2	Cores	15

12.11.3	Windings	15

12.11.4	Tanks	15

12.11.5	Drying Out and Oil Filling	15

12.12	Protective Coatings on Exposed Surfaces	15

12.12.1	General	15

12.12.2	Paint Colour	15

12.12.3	Surface Preparation	16

12.13	Protective Coatings on Internal Surfaces	16

12.13.1	Surface Preparation	16

12.13.2	Paint Coating	16

13	OUTPUT CURRENT TRANSFORMERS	16

14	TESTING	16

14.1	Type Tests General	16

14.2	Type Tests MEPS	16

14.3	Short Circuit Test	16

14.4	Routine Tests	17

14.5	Test Certificates	17

15	LIQUIDATED DAMAGES FOR EXCESS LOSSES	17

16	INSTALLATION AT SITE	17

17	POST INSTALLATION REQUIREMENTS	17

17.1	Final Inspection	17

17.2	Final Testing and Commissioning	17

17.3	As-Constructed Drawings	18

17.4	Manuals	18

18	SPECIAL REQUIREMENTS	18

# GENERAL

(a)	This Specification covers the requirements for the design, manufacture, assembly, inspection and factory testing of a ground mounted, oil filled, sealed, step down transformer, rated not more than 10 MVA.

(b)	This Specification also covers requirements for packaging, delivery to site, on site positioning, on site testing and commissioning.

In such cases the connection of the transformer at site will be carried out by others after on site assembly and positioning of the transformer has been completed by the Contractor and the Contractor shall return to site to commission the transformer once the connection of  the transformer has been completed.

# SITE

The location of and access to the site for the installation of the transformer shall be as shown in the Annexure.

# WORK BY THE PRINCIPAL

The work to be performed by the Principal shall be as detailed in the Annexure.

# INFORMATION TO BE PROVIDED BY THE CONTRACTOR

The Contractor shall provide the following documentation in respect to the transformer within the listed number of days after receipt of the Principal's order.

(a)	General Arrangement Drawings 					28 days

(b)	Electrical Wiring & Schematic Drawings 				28 days

(c)	Manufacture and Delivery Schedule 					14 days

(d)	Specification Data Sheets 						35 days

(e)	Inspection and Test Plan 							35 days

(f)	Test Certificates 								Within 14 days after Delivery

(g)	Operating and Maintenance Manual 					Within 14 days after Delivery

# CONTRACTOR’S DRAWINGS

The Contractor shall submit two A3 copies of the Contractor’s Drawings for approval.

The Contractor’s Drawings shall show the general arrangement, circuit diagrams and equipment specifications.

All drawings submitted by the Contractor shall be in accordance with the latest issue of the relevant Australian Standards.

Adequate contract shall be maintained between drawing detail and background, and the clarity and quality of drawings shall enable the Principal to microfilm the prints and reproduce, by photographic processes, clear and legible A3 copies for record purposes.

The drawings shall provide, in the title block, the number and title of the Contract, as well as details to identify the drawing, its contents, revision status and date of issue.

All drawings shall be prepared using AutoCAD Release 2000 or later software.  Drawings shall be prepared on A1 metric size drawing sheets, incorporating the Principal’s border and title block.

# STANDARDS

The workmanship, equipment and materials provided in accordance with this Specification shall comply in design, construction, rating and performance with the current relevant Australian Standards and Codes. In their absence, relevant International Standards together with the requirements of competent Authorities having jurisdiction over all or part of the manufacture, installation and operation of the equipment shall be adhered to. Compliance with Standards and Regulations shall include all amendments after the date of tender.

Specific reference is made within the Specification to the following Australian and International Standards:

AS 1627.4 		Metal-Finishing - Preparation and Pre-treatment of Surfaces Abrasive Blast Cleaning

AS 1767 		Insulating Oil for Transformers and Switchgear (incorporating Amendment 1)

AS 2374.1.2         Power transformers - Minimum energy performance standards (MEPS), requirements for distribution transformers

AS 2700               Colour standard for general purposes

AS 60044.1          Instrument transformers - Current transformers (IEC 60044.1 modified)

AS 60076.1          Power transformers - General (IEC 60076.1 modified)

AS 60529		Degree of Protection Provided by Enclosures for Electrical Equipment (IP Code)

AS/NZS 2312	Guide to the Protection of Iron and Steel Against Exterior Atmosphere Corrosion

AS 60076.10	Power Transformers – Determination of sound levels

AS/NZS 3750 	Paints for Steel Structures

AS/NZS ISO 9001	 Quality Management Systems - Requirements

EN 50181                Plug in type bushings above 1 kV and up to 52 kV and from 250 A to 2.5 kA – for equipment other than liquid filled transformers

IEC 60815             Guide for the selection of insulators in respect of polluted conditions

IEEE std C57-110	  Recommended Practice for establishing transformer capability when supplying non sinusoidal loads

ISO 9223	           Corrosion of metals and alloys - Corrosivity of atmospheres -Classification, determination and estimation

AS/NZS 3000	Electrical Installations - Buildings, Structures and Premises (Wiring Rules)

# QUALITY ASSURANCE

The transformer shall be manufactured under a Quality System certified by an Accredited Authority in accordance with AS/NZS ISO 9001 or an approved equivalent.

# SAFETY REQUIREMENTS – ELECTRICAL WORK

All electrical work shall be performed by appropriately qualified and experienced personnel who shall hold a current electrical workers license to perform such work.

# POWER SUPPLY

The transformer shall be suitable for operation from a High Voltage power supply and have the following characteristics:

(a)	Voltage range: ± 10% of primary voltage detailed in the Annexure.

(b)	Frequency range: 50 Hz ± 2½%.

(c) 	Earth fault factor  as detailed in the Annexure

# OPERATING MODE

The transformer shall be suitable for both continuous and cyclic operation at full load in the mode(s) of operation specified in the Annexure and under the specified ambient conditions.

# SITE AMBIENT CONDITIONS

a)	The site ambient conditions shall be considered to be as follows:

(i)	outdoor shade temperature range: -5oC to + 50oC

(ii)	outdoor shade maximum average daily  temperature:  + 30oC

(iii)	maximum relative humidity of 90 % with periods of heavy condensation

(iv)	pollution level in accordance with IEC 60815: as specified in the Annexure.

(b)	As specified in the Annexure, the transformer shall be suitable for mounting:

(i)	outdoors in full sun,

(ii)	outdoors in an open shaded position, or

(iii)	indoors in a well ventilated position.

# TECHNICAL REQUIREMENTS

## Standards

The transformer shall be designed and constructed in accordance with all relevant current parts of AS 60076 and with the requirements listed hereunder.

## Linear Load kVA Rating

The transformer’s linear load kVA rating shall be rated for 50 oC

## Non-linear Load Output Current Rating

If the transformer has been specified in the Annexure to be rated for supplying a non-linear current load, its output current rating shall be the linear load output current rating, as determined from the linear load kVA rating, further derated to take account of the increase in losses due to the harmonic currents. The amount of derating required will depend on the harmonic profile of the load current which is specified in terms of the factors detailed clause 12.5 hereunder.

The transformer maximum allowable non-linear current shall be determined in accordance with IEEE C57-110, as detailed hereunder.

## Types of Load Losses

In accordance with IEEE Std. C57-110, transformer rated linear load losses shall be divided into four categories as follows;

(i) 	no load losses Pnl

(ii) 	winding I2R losses Pw-r

(iii)  	winding eddy current losses Pec-r

(iv) 	other stray losses Posl-r

## Load Harmonic Profile Factors

### General

Applicable load harmonic profile factors are described hereunder and shall be used in the calculation of the rating of the transformer supplying a non-linear current having the associated harmonic profile.

Applicable load harmonic profile factors values are specified in the Annexure

### RMS Current Loss Factor

Frms = Σ(Ihr / If )2

for all values of Ihr and hn from hn = 1 up to  hn = 31

where hn = the harmonic number

Ihr = Ih /If

= ratio harmonic current to fundamental current

If = fundamental current

Ih = harmonic current at harmonic number hn

### Eddy Current Loss Factor

Fec = Σ(Ihr 2*hn2 )

for all values of Ihr and hn from hn = 1 up to  hn = 31

where hn = the harmonic number

Ihr = Ih /If

= ratio harmonic current to fundamental current

If = fundamental current

Ih = harmonic current at harmonic number hn

### Other Stray Loss Factor

Fosl = Σ(Ihr 2*hn0.8)

for all values of Ihr and hn from hn = 1 up to hn = 31

where hn = the harmonic number

Ihr = Ih /If

= ratio harmonic current to fundamental current

If = fundamental current

Ih = harmonic current at harmonic number hn

### Calculation of Load Losses

(a)	Winding I2R losses for a particular duty non-linear current

(Pw-d) shall be determined as follows:

Pw-d = Pw-r  *Frms * (Irms-d)2

where Irms-d = RMS value of duty load current

Pw-r  = rated I2R losses

(b) 	Winding eddy current losses for a particular duty non-linear current (Pec-d) will determined as follows:

Pec-d = Pec-r  *Fec *(Irms-d)2

where Irms-d = RMS value of duty load current

Pec-r = rated eddy current losses.

(c) 	Other stray losses for a particular duty non-linear current (Posl-d) will determined as follows:

Posl-d = Posl-r  *Fosl *(Irms-d)2

where Irms-d = RMS value of duty load current

Pec-r  = rated eddy current losses.

## Functional Requirements

The transformer shall comply with the following functional requirements:

- Number of phases :3

- Supply frequency : 50 Hz

- Number of windings :  as specified in the Annexure

- Vector group: as specified in the Annexure

- Voltages :

- primary: as specified in the Annexure

- secondary:  as specified in the Annexure

- tertiary winding : if applicable, as specified in the Annexure

- Connection:

- primary:  as specified in the Annexure

(ii) 	secondary:  as specified in the Annexure,  neutral brought out  if star connected

- tertiary: as specified in the Annexure

- Linear load kVA rating: as determined para. 12.2 above

- Non-linear load output current rating: as determined para. 12.3 above

## Transformer Service Conditions

The transformer shall be suitable for operation under the following service conditions:

- Service ambient conditions as determined para. 11 above

- HV supply earth fault factor as specified in the Annexure

- Grounding of secondary winding: as specified in the Annexure

- Grounding of tertiary winding, if applicable: as specified in the Annexure

- Type of load: as specified in the Annexure

## Design

The transformer shall be in accordance with the following design requirements:

- General; low loss design with minimum eddy current losses

- Type of magnetic circuit: low flux density core type core type

(c) 	Cooling: ONAN employing natural cooling oil

(d) 	Impedance: as specified in the Annexure

(e) 	Voltage tappings:

(i)	range : +/- 5%

(ii) 	step size : 2.5%

- tapped winding : primary

- Degree of Protection in accordance with AS 60529: IP66, transformer cable boxes: IP56

## Performance Requirements

The transformer’s performance shall be in accordance with the following requirements:

- Inrush current : not more than 7 times full load current

- If transformer rated < 2500 kVA at 11 kV or 22 kV,
minimum linear load efficiency  at 50 % FLC: as per AS 2374.1.2, Table 3
If transformer rated > 2500 kVA, at 11 kV or 22 kV,
minimum linear load efficiency  at 50 % FLC: 99.5 %
If transformer rated at 33 kV,
minimum linear load efficiency  at 50 % FLC: 99.5 %

- Lightning impulse withstand voltage (LIWV): as specified in the Annexure, full wave lightning impulse

- Short duration 50 Hz withstand voltage:  as specified Table 2, AS 60076.3, column 5, applied voltage or line terminal AC withstand

(e) 	Full load oil temperature limit:  100oC

(f) 	Full load winding temperature limit:  105oC

(g) 	Sound level as per AS/NZS 60076-10 Annex ZA1: reduced limit

## Miscellaneous Fittings

The transformer shall be fitted with the following:

(a)	High Voltage bushings having the EN 50181 Type C standard profile so as to be suitable for use with fully screened dead break elbow cable box terminations with “piggy back” surge diverters.

(b)	At Low Voltage terminations air insulated bushings within AS60529 – IP56 rated air insulated connector boxes suitable for connecting cabling or bus duct as specified in the Annexure.

(c)	Manual off circuit tapping switch brought out via an oil tight gland and complete with warning label located next to the handle indicating that the transformer must be de-energised before operating the switch.

(d)	An earthed screen between the primary and secondary windings (only if the type of load has been specified in the Annexure as non-linear).

(e)	A transformer tank earthing lug suitable for connection of earthing cable.

(f)	100mm dial type thermometer with top oil temperature indicator.

(g)	Alarm and trip change over contacts on the above thermometer, only if the transformer is rated > 315 kVA

(h)      Resealing pressure relief valve with operation indicator.

(i)	Alarm and trip change over contacts on the above pressure relief valve, only if the transformer is rated > 315 kVA.

(j)      Oil filling hole and cap.

(k)	Oil level indicator.

(l)	Oil drain valve with a sampler.

(m)	Lifting lugs.

(n)	Skid type base suitable for direct bolting into a prefabricated substation, if the transformer has been specified in the Annexure to be installed in same, otherwise suitable for direct bolting on to a concrete base.

(o)	Stainless steel rating plate.

(p)	Terminal marking plate.

(q)	The surge arresters specified in the Annexure are to be installed in the immediate vicinity of the transformer HV terminals. The surge arresters shall be connected directly to the transformer earth.

## Construction Requirements

### General

The core, windings, tank, framework, clamping arrangements and general structure of the transformers, when assembled, shall form a rigid construction which shall minimize vibration and shall be unaffected by normal use, short circuit conditions or handling during transport, installation, inspection or repair.

### Cores

The cores shall be constructed of high grade, cold rolled grain orientated silicon steel coated with temperature resistant inorganic insulation. The structure shall be formed into legs which are interconnected to the yokes with mitred joints. The active parts of the core shall be insulated from the structural support except for the earthing straps and any bolts passing through the core shall be fully insulated from it. The cores shall be so designed and constructed as to ensure that excessive temperatures do not occur at the centres of the cores. Facilities shall be provided for lifting the cores, with windings, from the tanks for inspection and repair.

### Windings

Windings shall be wound in the same direction. Winding assemblies shall be dried and shrunk during construction so that shrinking during the life of transformer will be minimal. Convenient means shall be provided to take up any slackness that does occur due to shrinkage of the windings.

### Tanks

The tank, which shall be of the sealed type, shall be constructed of steel plate, without conservators or breathers.

The tank and radiators shall be constructed in such a manner that the transformer internal pressure may vary between 50 kPa vacuum and 115 kPa positive pressure without damage or oil leakage for a fin-wall style of design or, 0 kPa vacuum and 150 kPa positive pressure in case of panel style of cooling radiators.

Joints and stiffeners shall be continuously welded along the upper line of contact with the tank to prevent lodging of waster behind the bracing. The undersides may be tack welded. Joints between the tank and tank covers and the flanges of bushings shall be rendered oil tight by the insertion of gaskets of neoprene or similar material that is impervious to and unaffected by transformer oil. The gaskets shall be under controlled pressure.

All parts of the tank shall be so designed and constructed as to eliminate the formation of air pockets inside the tank.

The tank covers shall be removable independently of the cores and windings.

### Drying Out and Oil Filling

The transformer shall be dried out thoroughly at the Contractor's works before filling with oil. The transformer shall be filled with oil in such a manner as to prevent air inclusion in the coil/core assembly.

## Protective Coatings on Exposed Surfaces

### General

The exposed metal surfaces shall be protected by the application of a painting system either Type LP1-A or LP2-A in accordance with AS2312. All paints comprising the paint system shall be from the same manufacturer.

The paint coating shall be rated as providing medium term, protection in tropical, industrial, marine and severe marine environments in accordance with AS/NZS 2312 (and ISO 9223).

### Paint Colour

The colour of the top coat paint applied to external surfaces shall be a standard colour in accordance with AS2700 as specified in the Annexure.

### Surface Preparation

All exposed metal surfaces shall be abrasive blast cleaned in accordance with AS 1627.4 Class 2.5.

## Protective Coatings on Internal Surfaces

### Surface Preparation

All tank internal surfaces above oil level shall be abrasive blast cleaned in accordance with AS 1627.4 Class 2.5.

### Paint Coating

A protective paint coating consisting of a zinc phosphate/micaceous iron oxide epoxy primer conforming to AS 3750.13.  Type 2 shall be applied to minimum dry film thickness of 20 microns to all tank internal surfaces above oil level surfaces.

# OUTPUT CURRENT TRANSFORMERS

- If the transformer is rated > 315 kVA, has a Low Voltage winding,the transformer shall be provided with protection class current transformers measuring the Low Voltage current in each phase.

These current transformers shall be located in the Low Voltage cable box

- If the transformer has a High Voltage secondary winding, the transformer shall be provided with protection class current transformers measuring the High Voltage secondary winding current in each phase.

These current transformers shall be located in a suitable compartment on the line side of the transformer High Voltage output bushings.

(c) 	The above current transformers shall be class 5P protection current transformers in accordance with AS 60044.1, shall have 1 Amp rated secondary windings and shall comply with other requirements as specified in the Annexure

# TESTING

## Type Tests General

Evidence shall be submitted on delivery indicating that all type tests required by AS 60076.1 have been carried out satisfactorily on the transformer or on a transformer of an identical design.

## Type Tests MEPS

If the transformer is rated < 2,500 kVA, evidence shall be submitted on delivery that efficiency testing in accordance with AS 2374.1.2 has been carried out satisfactorily on the transformer or on a transformer of identical design.

## Short Circuit Test

The AS/NZS 60076.5, Ability to Withstand Short Circuit, identifies the requirements for transformers to sustain without damage the effects of overcurrents originated by external short circuit.

The transformer manufacturer shall submit:

- a short circuit withstand capability test certificate of the proposed transformer design, or

- the theoretical evaluation of the ability of a power transformer to withstand the dynamic effects of short circuit and the thermal ability of a transformer. The documentation needed for the purpose includes all necessary technical data, such as electromagnetic design data sheets, calculations od short circuit currents, electromagnetic forces and mechanical stresses, supplemented by drawings, material specifications, manufacturing practices and process instructions, etc., either produced for the specific purpose of the electromagnetic and mechanical design of the transformer or as part of the manufacturer’s technology documentation.

## Routine Tests

Prior to the delivery, the transformer shall undergo all  routine tests required byAS 60076.1

## Test Certificates

All test certificates shall describe the tests carried out and the test results obtained.

# LIQUIDATED DAMAGES FOR EXCESS LOSSES

In addition to any liquidated damages specified in the General Conditions of Contract, the Contractor shall be liable to the Principal for liquidated damages in respect to cost of the amount of transformer total losses in excess of the value quoted previously by the Contractor in the Tender Response Schedule.

Such liquidated damages shall be calculated on the basis of the capitalised cost of losses quoted in the Annexure.

# INSTALLATION AT SITE

The Contractor shall deliver the transformer to the site, and then uncrate the transformer and position the associated equipment as necessary.

The Contractor shall place the transformer on the concrete base prepared by others and shall align it appropriately in accordance with approved drawings.

# POST INSTALLATION REQUIREMENTS

## Final Inspection

Before final testing and commissioning of the transformer takes place, the Contractor shall undertake an inspection to verify that the transformer has been installed correctly and is undamaged.

## Final Testing and Commissioning

The Contractor shall carry out the following tests after final inspection has been completed:

(a)	Insulation Resistance Check

(b)	Voltage Ratio Check

Once final inspection and final testing has been completed, the Contractor shall commission the transformer in conjunction with the Principal’s electrical staff.

## As-Constructed Drawings

The Contractor shall provide as constructed information on all drawings.

As-constructed drawings shall be supplied both electronically and as A3 size hard copies.

## Manuals

The Contractor shall supply 3 copies of comprehensive instruction manuals, written in English and covering the complete operation and maintenance requirements of all equipment supplied under the Contract. The manuals shall be printed on high grade A4 size paper and shall be bound in a high grade A4 size loose leaf binder.

Information included in the manuals shall include:

(a)	operating instructions;

(b)	safety instructions and warnings;

(c)	maintenance instructions and schedules;

(d)	recommended spare parts and special tool list;

(e)	as constructed drawings;

(f)	detailed equipment performance specifications and;

(g)	test reports and test certificates.

# SPECIAL REQUIREMENTS

In addition to the above the transformer shall be supplied in accordance with any special requirements detailed in the Supplementary Annexure.

Annexure to Specification

for

Ground Mounted Oil Filled Transformer

Project:…….…………………………………………………………………………………………………….

…………………………………………………………………………………………………………………….

Site Location:…..………………………………………………………………………………………………...

………………………………………………………………………………………………..…………………..

Type of Access to Site:………………………………………………………………………………………….

Work to be done by the Principal:………………………………………………………….…………………

………………………………………….……………………………………………………….……………….

………………………………………….…………………………………………………….………………….

…………………………………………..…………………………………………………….………………….

Capitalised Cost of Losses:	……………………………………………………………………………….$/kW

Location:

Type (i.e. outdoors in an open shaded position, 
outdoors in full sun, or indoors)…………………………………..…………………….………………………….

Pollution level in accordance with IEC 60815…..…………………………………….……………………………

Operating Mode:  	 Single or parallel operation….………………….…………………...………………..

Linear or non linear load….……………………….………………………………….

RMS current loss factor, Frms… ………………………………………….………………………………………………

Eddy current harmonic loss factor Fec….…………………………………….……………………………………..

Other stray losses harmonic loss factor Fosl….………………………………….……………………………….

H.V. Electrical Supply Conditions:

Highest voltage for equipment Um …………………………..………………………kV

System fault level…………………………………………………..……………...MVA

Method of system earthing……………………………………………………..……….

Earth fault factor…………………...………………………………..………………….

Annexure to Specification

for

Ground Mounted Oil Filled Transformers

Transformer Requirements

Winding Connections

Number of Windings:……..………………….……………………………………………………..…………………

Vector Group in accordance with AS 60076.1 Annex ZA:……………...……………..……………………………..

Primary Winding

Rated Voltage:……..……………………………………………………….………………………………………kV

Connection:…………………………………………………………………………………………………………...

Terminals to be Brought Out:………………………………………………………………………………………..

Linear load continuous rating:.………………………………………………………………………………………

Cable conductor size………………………………………………………………………………………….….mm2

Number of cables per phase…………………………………………………………………………………………..

Number of cables for neutral (if applicable)..…………………………………………………………........................

Surge Diverters (Required or not required)...………………………………………………………………………....

If required Type of Surge Diverter per phase ………………………..…………………..…………………

LIVW (AS 60076.3 Table 2 refers):.………………………………………….………………………………………

Secondary Winding

Rated Voltage:.…………………………………………………………………………………………………….kV

Connection:…………………………………………………………………………………………………………….

Terminals to be Brought Out:.	……………………………………………………………………….Cable conductor size……………………………..………………………………………………………………………………….mm2

Number of cables per phase………………………………………………………………………………………….

Number of cables for neutral (if applicable) ………………………………………………………………………...

If required Type of Surge Diverter per phase ………………………………………….…………………..………...

Linear load continuous rating: ……………………………………………………………………………………….

Maximum allowable non-linear current: ……………………………………………………………………….Amps

LIWV (AS 60076.3 Table 2 refers): …………………………………………………………………………………

Tertiary Winding

Rated Voltage:0…………………………………………………………………………………………………….kV

Connection:..……………………..……………………………………………………………………………………

Terminals to be Brought Out:..………………………..………………………………………………………………

Cable conductor size…………………………………………………………………………..………………….mm2

Number of cables per phase…………………………………………………………………………………………..

Number of cables for neutral (if applicable).…………………………………………………………........................

If required Type of Surge Diverter per phase………………………………..…………………..…………………….

Linear load continuous rating:.……………………………….………………………………………….……….kVA

Maximum allowable non-linear current:.……………………………………………………………………… Amps

LIWV (AS 60076.3 Table 2 refers):………………......................…………………………………………………kV

Oil Temperature Instrument Contacts

Warning contacts (required or not).	…………………………………………………………………………….

Trip contacts (required or not).	………………………………………………………………………………...

Pressure Instrument Contacts.

Trip contacts (required or not).…………………………………………………………………………………

Winding Temperature Monitoring

Warning/alarm contacts..…………………………………………………………………………………….

Trip contacts.………………………………………………………………………………………………...

Annexure to Specification

for

Ground Mounted Oil Filled Transformers

General

Overall Impedance: …………………………………………………………………………………………….%

Losses for Transformers > 2500 kVA:

Maximum Iron Loss at No Load:…..………………………………………………………………………..Watts

Minimum Iron Loss at 100% Load:..………………………………………………………………………..Watts

Maximum Copper Loss at 100% Load:…..…………………………………………………………………Watts

Maximum Audible Sound Power Level in accordance with AS 60076 (i.e. standard or special reduced):……….
……………………………………………………………………………………………………………………....

Type of Termination Required

At Primary Winding Termination…….………………………………………………………………..

At Secondary Winding Transmission…………………………………………………………………..

At Tertiary Winding Termination…….………………………………………………………………...

Special Requirements (i.e. nil or as per Supplementary Annexure).……………………………................................

Current Transformer Requirements ……………………………….…………………………………………………

Annexure to Specification

for

Ground Mounted Oil Filled Transformer

Project:………….………………………………………………………………………………….

……………………………………………………………………………………………………….

Special Requirements

Special Requirements in respect to this project are as hereunder:

……………………………………………………………………………………………………..

……………………………………………………………………………………………………..

……………………………………………………………………………………………………..

……………………………………………………………………………………………………..

……………………………………………………………………………………………………..

……………………………………………………………………………………………………..

……………………………………………………………………………………………………..

……………………………………………………………………………………………………..

……………………………………………………………………………………………………..

……………………………………………………………………………………………………..

……………………………………………………………………………………………………..

……………………………………………………………………………………………………..

……………………………………………………………………………………………………..

……………………………………………………………………………………………………..

……………………………………………………………………………………………………..

……………………………………………………………………………………………………..

……………………………………………………………………………………………………..

……………………………………………………………………………………………………..

……………………………………………………………………………………………………..

……………………………………………………………………………………………………..

……………………………………………………………………………………………………..

……………………………………………………………………………………………………..

……………………………………………………………………………………………………..

……………………………………………………………………………………………………..

……………………………………………………………………………………………………..

| Type Specification for Ground Mounted Oil Filled Transformer Tender Technical Response Schedule |
| --- |
| Clause | Subject | Noted | Compliance | Comments |
| No. |  |  | Yes | No |  |
| 1 | Scope |  |  |  |  |
| 2 | Site |  |  |  |  |
| 3 | Work by the Principal |  |  |  |  |
| 4 | Information from Contractor |  |  |  |  |
| 5 | Contractor’s Drawings |  |  |  |  |
| 6 | Standards |  |  |  |  |
| 7 | Quality Assurance |  |  |  |  |
| 8 | Safety Requirements |  |  |  |  |
| 9 | Power Supply |  |  |  |  |
| 10 | Operating Mode |  |  |  |  |
| 11 | Site Ambient Conditions |  |  |  |  |
| 12 | Technical Requirements |  |  |  |  |
| 12.1 | Standards |  |  |  |  |
| 12.2 | Linear Load kVA Rating |  |  |  |  |
| 12.3 | Non-Linear Current Rating |  |  |  |  |
| 12.4 | Types of Load Losses |  |  |  |  |
| 12.5 | Load Harmonic Profile Factors |  |  |  |  |
| 12.6 | Functional Requirements |  |  |  |  |
|  | 3 phases |  |  |  |  |
|  | Operating frequency |  |  |  | Rated Hz = |
|  | Vector Group |  |  |  | Vector group = |
|  | Number of windings |  |  |  | No. windings = |
|  | Voltages |  |  |  | Primary rated primary kV = |
|  |  |  |  |  | Secondary connection = |
|  |  |  |  |  | Tertiary rated kV = |
|  | Connection |  |  |  | Primary connection = |
|  |  |  |  |  | Secondary connection = |
|  |  |  |  |  | Tertiary connection = |
|  | Linear Load kVA |  |  |  | Primary rated kVA = |
|  |  |  |  |  | Secondary rated kVA = |
|  |  |  |  |  | Tertiary rated kVA = |
|  | Non-Linear Load Amps |  |  |  | In max Amps = |
| 12.7 | Transformer Service Conditions |  |  |  |  |
|  | Service Ambient Conditions |  |  |  |  |

| Type Specification for Ground Mounted Oil Filled Transformer Tender Technical Response Schedule |
| --- |
| Clause | Subject | Noted | Compliance | Comments |
| No. |  |  | Yes | No |  |
|  | Supply Earth Fault Factor |  |  |  |  |
|  | Secondary Winding Grounding |  |  |  |  |
|  | Tertiary Winding Grounding |  |  |  |  |
|  | Type of Load |  |  |  |  |
| 12.8 | Design |  |  |  |  |
|  | Low Loss Design |  |  |  | FLC efficiency % = |
|  |  |  |  |  | No load 50 Hz losses, kW = |
|  |  |  |  |  | Full load 50 Hz losses, kW = |
|  | Flux density |  |  |  | Flux density T = |
|  | Type of cooling |  |  |  |  |
|  | Impedance primary/secondary winding |  |  |  | Impedance % = …… at ……kVA |
|  | Impedance primary/tertiary winding |  |  |  | Impedance % = …… at ……kVA |
|  | Impedance secondarty/tertiary winding |  |  |  | Impedance % = …… at ……kVA |
|  | Voltage Tappings |  |  |  |  |
|  | Range |  |  |  | Tapping range % = |
|  | Size |  |  |  | Tapping step % = |
|  | Tapped Primary Winding |  |  |  |  |
|  | Degree of Protection |  |  |  | IP = |
| 12.9 | Performance Requirements |  |  |  |  |
|  | Inrush Current |  |  |  | Inrush current % = |
|  | Linear Load Efficiency |  |  |  | 100% load efficiency % = |
|  |  |  |  |  | 50% load efficiency % = |
|  | Lightning Impulse Withstand |  |  |  | LIWV, kVp = |
|  | Short Duration 50 Hz Withstand Voltage |  |  |  | Primary 50 Hz withstand kVrms = |
|  |  |  |  |  | Secondary 50 Hz withstand kVrms = |
|  |  |  |  |  | Tertiary 50 Hz withstand kVrms = |
|  | Oil Temperature Limits |  |  |  | Max. oil temp, deg C = |
|  | Winding Temperature Limit |  |  |  | Max. winding temp, deg C = |
|  | Sound Level |  |  |  | Reduced sound power level, dBA = |
| 12.10 | Miscellaneous Fittings |  |  |  |  |
|  | HV terminations |  |  |  | HV bushings = |
|  |  |  |  |  | HV dead break elbow = |
|  | HV Surge Diverters |  |  |  | Max. operating kV = |
|  |  |  |  |  | Temp over voltage kV = |
| Type Specifications for Ground Mounted Oil Filled Transformer Tender Technical Response Schedule |
| Clause | Subject | Noted | Compliance | Comments |
| No. |  |  | Yes | No |  |
|  |  |  |  |  | Discharge Amps = |
|  |  |  |  |  | Maximum residual kV = |
|  | L.V. terminations |  |  |  | LV bushings = |
|  | Tapping switch |  |  |  |  |
|  | Earth screen |  |  |  |  |
|  | Tank earth connection |  |  |  |  |
|  | Dial type thermometer |  |  |  | Alarm temperature deg C = |
|  |  |  |  |  | Trip temperature deg C = |
|  | Pressure of relief valve with trip contacts |  |  |  | Trip pressure kPa = |
|  | Oil filling hole |  |  |  |  |
|  | Oil level indicator |  |  |  | Type = |
|  | Oil Drain Valve with sampler |  |  |  |  |
|  | Lifting Lugs |  |  |  |  |
|  | Skid Base |  |  |  |  |
|  | Stainless steel Rating Plate |  |  |  |  |
|  | Terminal Marking Plate |  |  |  |  |
| 12.11 | Construction Requirements |  |  |  |  |
| 12.11.1 | General |  |  |  |  |
| 12.11.2 | Cores |  |  |  |  |
| 12.11.3 | Windings |  |  |  |  |
| 12.11.4 | Tanks |  |  |  |  |
| 12.12 | Protective Coatings on Exposed Surfaces |  |  |  |  |
| 12.12.1 | General |  |  |  | AS/NZS 2312 System = |
|  |  |  |  |  | Classification = |
|  |  |  |  |  | Primer DFT microns = |
|  |  |  |  |  | Intermediate DFT microns = |
|  |  |  |  |  | Top coat DFT microns = |
|  |  |  |  |  | Total DFT microns = |
| 12.12.2 | Paint Colour |  |  |  | AS 2700 No. = |
| 12.12.3 | Surface Preparation |  |  |  |  |
| 12.13 | Protective Coatings on Internal Surfaces |  |  |  |  |
| 12.13.1 | Surface Preparation |  |  |  |  |
| 12.13.2 | Paint Coating |  |  |  | DFT microns = |
| 13. | Output Current Transformers |  |  |  | CT primary Amps = |
|  |  |  |  |  | CT secondary Amps = |
|  |  |  |  |  | CT auxiliary class = |

| Type Specification for Ground Mounted Oil Filled Transformer Tender Technical Response Schedule |
| --- |
| Clause | Subject | Noted | Compliance | Comments |
| No. |  |  | Yes | No |  |
|  |  |  |  |  | CT burden, VA = |
| 14. | Testing |  |  |  |  |
| 14.1 | Type Tests |  |  |  |  |
| 14.2 | Type Tests MEPS |  |  |  |  |
| 14.3 | Short Circuit Test |  |  |  | Test certificate or theoretical evaluation attached = |
| 14.4 | Routine Tests |  |  |  |  |
| 14.5 | Test Certificates |  |  |  |  |
| 15. | Liquidated Damages |  |  |  |  |
| 16. | Installation at Site |  |  |  |  |
| 17. | Post Installation Requirements |  |  |  |  |
| 17.1 | Final Inspection |  |  |  |  |
| 17.2 | Final Testing and Commissioning |  |  |  |  |
| 17.3 | As Constructed Information |  |  |  |  |
| 17.4 | Manuals |  |  |  |  |
|  | Dimensions |  |  |  | O/A length m = |
|  |  |  |  |  | O/A width m = |
|  |  |  |  |  | O/A height m = |
|  |  |  |  |  | Weight kg = |
| 18. | Special Requirements |  |  |  |  |

END OF DOCUMENT