## Guidance
Guidance Notes
REVISION STATUS
The revision status of this document is shown in the section below:
REVISION STATUS
VER/REV | DATE | TABS REVISED | REVISION DESCIRPTION | RVWD. | APPD.
1/1 | 2019-07-05 | Pump | Added new asset classes | MB
1/1 | 2019-07-05 | Motor | Added new asset classes | MB
2 | 2022-09-05 |  | Combined Appendix C, D & E | BY | MB
Task |  | Stage | Input |  | Responsibility
In-house/External Design |  | Engineering Design | Create equipment schedules |  | Designer
In-house/External Design |  | Detailed Design | Review and update equipment static & dynamic data |  | Designer
D&C Contract |  | Detailed Design | Create equipment schedules |  | D&C Contractor
Alliance Contract |  | Detailed Design | Create equipment schedules |  | Alliance Contractor
Delivery |  | Construction/ Commissioning | Update equipment schedules with as procured information. Send completed equipment schedule to Asset Registration Team |  | Contruction Contractor/ Commissioning Manager
Operational Asset change |  | Maintenance | Create equipment schedule for new asset and send to Asset Registration Team. |  | Team Leader
Asset Registration |  | Registration | Use equipment schedules to update SAP. |  | Asset Registration Team
Equipment schedules are required to be created for all new assets to enable Asset Registration in the Corporate Asset Database - SAP.
The following table identifies th roles an responsibilities of stakeholders to enable an asset to be registered, or attributes of an existing asset updated.

## Definitions
PROPERTY NAME | PROPERTY DESCRIPTION | UNITS
Asset ID | The ID for the asset object that the business knows it by | N/A
Description - Asset | The common name that the unit is referred to within the business | N/A
Date - Manufactured | Date that the asset was manufactured | DD/MM/YYYY
Date - Acquired | Date that asset acquired (purchased or gifted) by the business | DD/MM/YYYY
Date - Warranty Expire | Date which the warranty expires for the asset | DD/MM/YYYY
Date - Disposal | Date which business no longer has the asset as part it fleet | DD/MM/YYYY
Acquisitions Cost | The cost of acquiring the asset by the business | $
Depreciation Method | The type of depreciation method used for the unit | N/A
Expected Asset Life | The expected accounting life for the asset for asset valuation | Yrs
As-Constructed Reference | As-Constructed Drawing Record for the unit | N/A
Type of Pump | The physical type of pump | N/A
Manufacture / Make | The name of the manufacture / make of the unit | N/A
Model Number / ID | The model number for the unit | N/A
Serial Number | The serial number for the unit | N/A
Weight | Total weight of the pump including impeller | Kg
Material - Pump Casing | The material that the pump casing is made from. | N/A
Material - Lining | The material that is lining the pump volute | N/A
Diameter - Impeller Max. | The maximum size diameter Impeller that the pump can take | mm
Type of Impeller | The type of impeller that is designed for the pump. | N/A
Type of Seal | The type of seal installed as part of the pump | N/A
Pump Design Max. Flowrate | The Max. Flowrate that the pump is designed for | L/S
Pump Design Min. Flowrate | The Min. Flowrate that the pump is designed for | L/S
Pump Design Head at Max. Flow | The head that the pump is designed for at max. flowrate | MHW
Pump Design Head at Min Flow | The head that the pump is designed for at min. flowrate | MHW
Speed at Max. Flowrate | The pump speed at the designed for at max. flowrate | RPM
Type of Connection | The type of coupling connection on the Pump shaft | N/A
Type of Bearings | The type of bearings used within the pump to support the rotating element | N/A
Type of Wear Ring | The type of wear ring / surfaces within the pump | N/A
Mounting Configuration | The type of mounting configuration for the pump (Vertical / Horizontal) | N/A
Type of Motor | The physical type of motor | N/A
Power | The unit rated input energy / power consumed | kW
Rated Voltage | The unit rated voltage that it is designed to operate at. | Volts
Rated Current | The unit current rating to operate at (also known as Full Load Current) | Amps
Weight | Total weight of the unit | Kg
Ex Rating | Classification of the unit (motor) for its suitably to be used in Hazardous locations | N/A
Ingress Protection (IP) Rating | Classification of the capacity of the unit (motor) to resist ingress of dust and or water. | N/A
Insulation Class | Classification of the insulation used in the unit | N/A
Anti Condensation Heater | Indication if the motor has a heater to prevent moisture occurring within the unit | N/A
Type of Winding Protection | Describes the type of method used within the unit to protect the motor windings | N/A
Type of Brushes | The physical type brush used as part of the unit | N/A
Type of Cooling | The type of motor cooling system installed with the unit | N/A

## Electrical
ELECTRICAL SCHEDULE
ENGINEERING DESIGN | [8 empty] | ENGINEERING DESIGN DETAIL |  | PROCUREMENT
REVISION | P&ID DRAWING | TAG No. | FUNCTIONAL LOCATION | EQUIPMENT TYPE | EQUIPMENT DESCRIPTION | STATUS | POWER (kW) | VOLTAGE (V) | MAKE | MODEL | SERIAL No. | SUPPLIER | INSTALLED BY | DATASHEET | COMMENTS

## Instrument
INSTRUMENT SCHEDULE - FLUROSILICIC ACID: OVERALL
ENGINEERING DESIGN | [18 empty] | ENGINEERING DESIGN DETAIL |  | PROCUREMENT
REVISION | P&ID DRAWING | TAG No. | FUNCTIONAL LOCATION | EQUIPMENT TYPE | EQUIPMENT DESCRIPTION | STATUS | POWER (kW) | VOLTAGE (V) | PIPE SIZE | DESIGN PRESSURE (KPA) | DI | AI | DO | AO | INPUT | OUTPUT | RANGE | SCALE | MAKE | MODEL | SERIAL No. | SUPPLIER | INSTALLED BY | DATASHEET | COMMENTS
D | GT36-060-83.1 | HS83101 | FSA Storage Room | Hand Switch | Exhaust Fan
D | GT36-060-83.1 | NZ83101 | FSA Storage Room | Torque Actuator | Fan Motor Actuator
D | GT36-060-83.1 | YS83106 | FSA Storage Room | Contact | Load-in Door Switch | [5 empty] | 1
D | GT36-060-83.1 | LI83110 | FSA Storage Room | Level Indicator | Magnetic Level Indicator | [13 empty] | Ekotech/ Klinger or Equivalent | [5 empty] | No Glass
D | GT36-060-83.1 | LSHH83110 | FSA Storage Room | Level Switch High High | Sensing Level Switch |  |  | 24V DC |  |  | 1 | [7 empty] | Supplied with magnetic level indicator package
D | GT36-060-83.1 | LAHH83110A | FSA Storage Room | Level Alarm High High | Red light Tank 1 High High Level Alarm |  |  | 24V DC | [5 empty] | 1 |  |  |  |  | Mann Industries or Moore Industries
D | GT36-060-83.1 | LAHH83110B | FSA Storage Room | Level Alarm High High | Audible Tank 1 High High Level Alarm | [5 empty] | 1 |  |  | 1
D | GT36-060-83.1 | LT83113 | FSA Storage Room | Level Transmitter | Tank 1 Level Transmitter | [11 empty] | 0 - 5 | L | Rosemount, Yokogawa or Siemens | [5 empty] | Remote diaphragm seal to be used - must be FSA compatible; e.g. Monel, PTFE, etc.
D | GT36-060-83.1 | LI83113 | FSA Storage Room | Level Indicator | Tank 1 Load-in Panel Level Indicator
D | GT36-060-83.1 | HS83113 | FSA Storage Room | Hand Switch | Manual Push button for testing Tank 1 Alarms | [13 empty] | Siemens
D | GT36-060-83.1 | LAH83113 | FSA Storage Room | Level Alarm High | Red light Tank 1 High Level Alarm | [8 empty] | 1 |  |  |  |  | Siemens
D | GT36-060-83.1 | ZSH83117 | FSA Storage Room | Position Switch High | Part of Motorised Valve VA83117 |  |  |  | NA |  | 1 | [7 empty] | SUPPLIED WITH VALVE PACKAGE
D | GT36-060-83.1 | ZZ83117 | FSA Storage Room | Position Actuator | Part of Motorised Valve VA83117 |  |  |  | NA |  |  |  | 1 | [5 empty] | SUPPLIED WITH VALVE PACKAGE
D | GT36-060-83.1 | ZSL83117 | FSA Storage Room | Position Switch Low | Part of Motorised Valve VA83117 |  |  |  | NA |  | 1 | [7 empty] | SUPPLIED WITH VALVE PACKAGE
D | GT36-060-83.1 | ZSH83118 | FSA Storage Room | Position Switch High | Part of Motorised Valve VA83118 |  |  |  | NA |  | 1 | [7 empty] | SUPPLIED WITH VALVE PACKAGE
D | GT36-060-83.1 | ZZ83118 | FSA Storage Room | Position Actuator | Part of Motorised Valve VA83118 |  |  |  | 50/50/50 |  |  |  | 1 | [5 empty] | SUPPLIED WITH VALVE PACKAGE
D | GT36-060-83.1 | ZSL83118 | FSA Storage Room | Position Switch Low | Part of Motorised Valve VA83118 |  |  |  | NA |  | 1 | [7 empty] | SUPPLIED WITH VALVE PACKAGE
D | GT36-060-83.1 | LI83120 | FSA Storage Room | Level Indicator | Tank 2 Level Indicator | [6 empty] | LIT LOOP | [6 empty] | Ekotech or Klinger or equivalent | [5 empty] | No glass
D | GT36-060-83.1 | LSHH83210 | FSA Storage Room | Level Switch High High | Tank 2 Level Switch High High | [5 empty] | 1
D | GT36-060-83.1 | LAHH83210A | FSA Storage Room | Level Alarm High High | Red light Tank 2 High High Level Alarm | [7 empty] | 1
D | GT36-060-83.1 | LAHH83210B | FSA Storage Room | Level Alarm High High | Audible Tank 2 High High Level Alarm | [7 empty] | 1
D | GT36-060-83.1 | LT83213 | FSA Storage Room | Level Transmitter | Tank 2 Level Transmitter | [11 empty] | 0 - 5 | L | Rosemount, Yokogawa or Siemens | [5 empty] | Remote diaphragm seal to be used - must be FSA compatible; e.g. Monel, PTFE, etc.
D | GT36-060-83.1 | LI83213 | FSA Storage Room | Level Indicator | Tank 2 Load-in Panel Level Indicator | [6 empty] | LIT LOOP
D | GT36-060-83.1 | HS83213 | FSA Storage Room | Hand Switch | Manual Push button for testing Tank 2 Alarms | [13 empty] | Siemens
D | GT36-060-83.1 | LAH83213 | FSA Storage Room | Level Alarm High | Red light Tank 2 High Level Alarm | [8 empty] | 1 |  |  |  |  | Siemens
D | GT36-060-83.1 | ZSH83127 | FSA Storage Room | Position Switch High | Part of Motorised Valve VA83127 |  |  |  | NA |  | 1 | [7 empty] | SUPPLIED WITH VALVE PACKAGE
D | GT36-060-83.1 | ZZ83127 | FSA Storage Room | Position Actuator | Part of Motorised Valve VA83127 |  |  |  | NA |  |  |  | 1 | [5 empty] | SUPPLIED WITH VALVE PACKAGE
D | GT36-060-83.1 | ZSL83127 | FSA Storage Room | Position Switch Low | Part of Motorised Valve VA83127 |  |  |  | NA |  | 1 | [7 empty] | SUPPLIED WITH VALVE PACKAGE
D | GT36-060-83.1 | ZSH83128 | FSA Storage Room | Position Switch High | Part of Motorised Valve VA83128 |  |  |  | NA |  | 1 | [7 empty] | SUPPLIED WITH VALVE PACKAGE
D | GT36-060-83.1 | ZZ83128 | FSA Storage Room | Position Actuator | Part of Motorised Valve VA83128 |  |  |  | 50/50/50 |  |  |  | 1 | [5 empty] | SUPPLIED WITH VALVE PACKAGE
D | GT36-060-83.1 | ZSL83128 | FSA Storage Room | Position Switch Low | Part of Motorised Valve VA83128 |  |  |  | NA |  | 1 | [7 empty] | SUPPLIED WITH VALVE PACKAGE
D | GT36-060-83.1 | ZSH83132 | FSA Storage Room | Position Switch High | Part of Motorised Valve VA83132 |  |  |  | NA |  | 1 | [7 empty] | SUPPLIED WITH VALVE PACKAGE
D | GT36-060-83.1 | ZZ83132 | FSA Storage Room | Position Actuator | Part of Motorised Valve VA83132 |  |  |  | 25 |  |  |  | 1 | [5 empty] | SUPPLIED WITH VALVE PACKAGE
D | GT36-060-83.1 | ZSL83132 | FSA Storage Room | Position Switch Low | Part of Motorised Valve VA83132 |  |  |  | NA |  | 1 | [7 empty] | SUPPLIED WITH VALVE PACKAGE
D | GT36-060-83.1 | ZSH83134 | FSA Storage Room | Position Switch High | Part of Motorised Valve VA83134 |  |  |  | NA |  | 1 | [7 empty] | SUPPLIED WITH VALVE PACKAGE
D | GT36-060-83.1 | ZZ83134 | FSA Storage Room | Position Actuator | Part of Motorised Valve VA83134 |  |  |  | 25 |  |  |  | 1 | [5 empty] | SUPPLIED WITH VALVE PACKAGE
D | GT36-060-83.1 | ZSL83134 | FSA Storage Room | Position Switch Low | Part of Motorised Valve VA83134 |  |  |  | NA |  | 1 | [7 empty] | SUPPLIED WITH VALVE PACKAGE
D | GT36-060-83.1 | LSH83135 | FSA Storage Room | Level Switch High | Internal Bund Sump High Level Switch | [5 empty] | 1 | [7 empty] | Euo, Kelco or Flygt | [5 empty] | 3m cable length
D | GT36-060-83.1 | AE83136 | FSA Storage Room | Analysis Element | Internal Bund Sump Conductivity Element
D | GT36-060-83.1 | AIT83136 | FSA Storage Room | Analysis Indicating Transmitter | Internal Bund Sump Conductivity Indicating Transmitter | [11 empty] | 10 - 20,000 | uS/cm | Euo, Kelco or Flygt
D | GT36-060-83.1 | ZIC83137 | FSA Storage Room | Position Indicating Closed | Part of Motorised Valve VA83137 | [13 empty] | SUPPLIED WITH VALVE PACKAGE
D | GT36-060-83.1 | ZSL83137 | FSA Storage Room | Position Switch Low | Part of Motorised Valve VA83137 |  |  |  | NA |  | 1 | [7 empty] | SUPPLIED WITH VALVE PACKAGE
D | GT36-060-83.1 | ZSH83137 | FSA Storage Room | Position Switch High | Part of Motorised Valve VA83137 |  |  |  | NA |  | 1 | [7 empty] | SUPPLIED WITH VALVE PACKAGE
D | GT36-060-83.1 | ZZ83137 | FSA Storage Room | Position Actuator | Part of Motorised Valve VA83137 |  |  |  | 50 |  |  |  | 1 | [5 empty] | SUPPLIED WITH VALVE PACKAGE
D | GT36-060-83.1 | ZSL83138 | FSA Storage Room | Position Switch Low | Part of Motorised Valve VA83138 |  |  |  | NA |  | 1 | [7 empty] | SUPPLIED WITH VALVE PACKAGE
D | GT36-060-83.1 | ZSH83138 | FSA Storage Room | Position Switch High | Part of Motorised Valve VA83138 |  |  |  | NA |  | 1 | [7 empty] | SUPPLIED WITH VALVE PACKAGE
D | GT36-060-83.1 | ZZ83138 | FSA Storage Room | Position Actuator | Part of Motorised Valve VA83138 |  |  |  | 50 |  |  |  | 1 | [5 empty] | SUPPLIED WITH VALVE PACKAGE
D | GT36-060-83.1 | LSH83138 | FSA Storage Room | Level Switch High | Load-in Apron Sump High Level Switch | [5 empty] | 1
D | GT36-060-83.1 | LSH83144 | FSA Storage Room | Level Switch High | Waste Holding Tank High Level Switch | [5 empty] | 1 | [13 empty] | 3m cable length
INSTRUMENT SCHEDULE - FLUROSILICIC ACID: DOSING PANEL 1
ENGINEERING DESIGN | [18 empty] | ENGINEERING DESIGN DETAIL |  | PROCUREMENT
REVISION | P&ID DRAWING | TAG No. | FUNCTIONAL LOCATION | EQUIPMENT TYPE | EQUIPMENT DESCRIPTION | STATUS | POWER (kW) | VOLTAGE (V) | SIZE | DESIGN PRESSURE (KPA) | DI | AI | DO | AO | INPUT | OUTPUT | RANGE | SCALE | MAKE | MODEL | SERIAL No. | SUPPLIER | INSTALLED BY | DATASHEET | COMMENTS
B | GT36-060-83.2 | ZZ83202 | Dosing Panel 1 | Position Actuator | Part of Motorised Valve VA83202 |  |  |  | 50 |  |  |  | 1 | [5 empty] | SUPPLIED WITH VALVE PACKAGE
B | GT36-060-83.2 | ZSL83202 | Dosing Panel 1 | Position Switch Low | Part of Motorised Valve VA83202 |  |  |  | NA |  | 1 | [7 empty] | SUPPLIED WITH VALVE PACKAGE
B | GT36-060-83.2 | ZSH83202 | Dosing Panel 1 | Position Switch High | Part of Motorised Valve VA83202 |  |  |  | NA |  | 1 | [7 empty] | SUPPLIED WITH VALVE PACKAGE
B | GT36-060-83.2 | PI83204 | Dosing Panel 1 | Pressure Indicator | Pressure Indicator | [11 empty] | 0 - 300 | kPa | WIKA or Equivalent | [5 empty] | Diaphragm seal type required
B | GT36-060-83.2 | FI83205 | Dosing Panel 1 | Variable Area Flow Indicator | Dilution Water Supply Variable Area Flow Indicator |  |  |  | 50 | 1000kPa | [6 empty] | 0 - 5 | m3/h | ABB or Equivalent | [5 empty] | AS2129 Table E
B | GT36-060-83.2 | FSL83205 | Dosing Panel 1 | Flow Switch Low | Dilution Water Low Flow Switch |  |  |  | NA |  | 1
B | GT36-060-83.2 | YS83213A | Dosing Panel 1 | State Switch | Part of Pump PU83213
B | GT36-060-83.2 | YS83213B | Dosing Panel 1 | State Switch | Part of Pump PU83213
B | GT36-060-83.2 | YS83213C | Dosing Panel 1 | State Switch | Part of Pump PU83213
B | GT36-060-83.2 | SY83213 | Dosing Panel 1 | Speed Relay | Part of Pump PU83213
B | GT36-060-83.2 | HC83213B | Dosing Panel 1 | Hand Controller | Part of Pump PU83213
B | GT36-060-83.2 | IY83213 | Dosing Panel 1 | Current Relay | Part of Pump PU83213
B | GT36-060-83.2 | PI83216 | Dosing Panel 1 | Pressure Indicator | Pressure Indicator | [11 empty] | 0 - 500 | kPa | WIKA or Equivalent | [5 empty] | Diaphragm seal type required - must be FSA compatible; e.g. Monel, PTFE, etc.
B | GT36-060-83.2 | FE83218 | Dosing Panel 1 | Flow Element | Part of Magflow Dosing Panel 1 |  |  |  | 15 |  | 1 | [5 empty] | 0 - 50 | L/h | Danfoss, Krohne, Siemens or Equivalent | [5 empty] | Remote transmitter for flow indication AS2129 Table E
B | GT36-060-83.2 | FIT83218 | Dosing Panel 1 | Flow Indicating Transmitter | Part of Magflow Dosing Panel 1 | [5 empty] | 1 | [5 empty] | 0 - 50 | L/h | [6 empty] | Wall Mounting kit required
B | GT36-060-83.2 | FQT83218 | Dosing Panel 1 | Totalised Flow Transmitter | Part of Magflow Dosing Panel 1
B | GT36-060-83.2 | ZZ83224 | Dosing Panel 1 | Position Actuator | Part of Motorised Valve VA83224 |  |  |  | 15 |  |  |  | 1 | [5 empty] | SUPPLIED WITH VALVE PACKAGE
B | GT36-060-83.2 | ZSL83224 | Dosing Panel 1 | Position Switch Low | Part of Motorised Valve VA83224 |  |  |  | NA |  | 1 | [7 empty] | SUPPLIED WITH VALVE PACKAGE
B | GT36-060-83.2 | ZSH83224 | Dosing Panel 1 | Position Switch High | Part of Motorised Valve VA83224 |  |  |  | NA |  | 1 | [7 empty] | SUPPLIED WITH VALVE PACKAGE
INSTRUMENT SCHEDULE - FLUROSILICIC ACID: DOSING PANEL 2
ENGINEERING DESIGN | [18 empty] | ENGINEERING DESIGN DETAIL |  | PROCUREMENT
REVISION | P&ID DRAWING | TAG No. | FUNCTIONAL LOCATION | EQUIPMENT TYPE | EQUIPMENT DESCRIPTION | STATUS | POWER (kW) | VOLTAGE (V) | SIZE | DESIGN PRESSURE (KPA) | DI | AI | DO | AO | INPUT | OUTPUT | RANGE | SCALE | MAKE | MODEL | SERIAL No. | SUPPLIER | INSTALLED BY | DATASHEET | COMMENTS
B | GT36-060-83.3 | ZZ83302 | Dosing Panel 2 | Position Actuator | Part of Motorised Valve VA83302 |  |  |  | 50 |  |  |  | 1 | [5 empty] | SUPPLIED WITH VALVE PACKAGE
B | GT36-060-83.3 | ZSL83302 | Dosing Panel 2 | Position Switch Low | Part of Motorised Valve VA83302 |  |  |  | NA |  | 1 | [7 empty] | SUPPLIED WITH VALVE PACKAGE
B | GT36-060-83.3 | ZSH83302 | Dosing Panel 2 | Position Switch High | Part of Motorised Valve VA83302 |  |  |  | NA |  | 1 | [7 empty] | SUPPLIED WITH VALVE PACKAGE
B | GT36-060-83.3 | PI83304 | Dosing Panel 2 | Pressure Indicator | Pressure Indicator | [11 empty] | 0 - 300 | kPa | WIKA or Equivalent | [5 empty] | Diaphragm seal type required 1/2" NPT
B | GT36-060-83.3 | FI83305 | Dosing Panel 2 | Variable Area Flow Indicator | Dilution Water Supply Variable Area Flow Indicator |  |  |  | 50 | 1000kPa | [6 empty] | 0 - 5 | m3/h | ABB or Equivalent | [5 empty] | AS2129 Table E
B | GT36-060-83.3 | FSL83305 | Dosing Panel 2 | Flow Switch Low | Dilution Water Low Flow Switch |  |  |  | NA |  | 1 | [7 empty] | ABB or Equivalent
B | GT36-060-83.3 | YS83313A | Dosing Panel 2 | State Switch | Part of Pump PU83313
B | GT36-060-83.3 | YS83313B | Dosing Panel 2 | State Switch | Part of Pump PU83313
B | GT36-060-83.3 | YS83313C | Dosing Panel 2 | State Switch | Part of Pump PU83313
B | GT36-060-83.3 | SY83313 | Dosing Panel 2 | Speed Relay | Part of Pump PU83313
B | GT36-060-83.3 | HC83313B | Dosing Panel 2 | Hand Controller | Part of Pump PU83313
B | GT36-060-83.3 | IY83313 | Dosing Panel 2 | Current Relay | Part of Pump PU83313
B | GT36-060-83.3 | PI83316 | Dosing Panel 2 | Pressure Indicator | Pressure Indicator | [11 empty] | 0 - 500 | kPa | WIKA or Equivalent | [5 empty] | Diaphragm seal type required - must be FSA compatible; e.g. Monel, PTFE, etc.
B | GT36-060-83.3 | FE83318 | Dosing Panel 2 | Flow Element | Part of Magflow Dosing Panel 2 |  |  |  | 15 | 1000 | 1 | [5 empty] | 0 - 50 | L/h | Danfoss, Krohne, Siemens or Equivalent | [5 empty] | AS2129 Table E
B | GT36-060-83.3 | FIT83318 | Dosing Panel 2 | Flow Indicating Transmitter | Part of Magflow Dosing Panel 2 |  |  |  |  | 1000 | 1 | [5 empty] | 0 - 50 | L/h | [6 empty] | TUBE 1/2" PVC Wall Mounting Kit Required
B | GT36-060-83.3 | FQT83318 | Dosing Panel 2 | Totalised Flow Transmitter | Part of Magflow Dosing Panel 2
B | GT36-060-83.3 | ZZ83324 | Dosing Panel 2 | Position Actuator | Part of Motorised Valve VA83324 |  |  |  | 15 |  |  |  | 1 | [5 empty] | SUPPLIED WITH VALVE PACKAGE
B | GT36-060-83.3 | ZSL83324 | Dosing Panel 2 | Position Switch Low | Part of Motorised Valve VA83324 |  |  |  | NA |  | 1 | [7 empty] | SUPPLIED WITH VALVE PACKAGE
B | GT36-060-83.3 | ZSH83324 | Dosing Panel 2 | Position Switch High | Part of Motorised Valve VA83324 |  |  |  | NA |  | 1 | [7 empty] | SUPPLIED WITH VALVE PACKAGE
INSTRUMENT SCHEDULE - FLUROSILICIC ACID: ANCILLARIES
ENGINEERING DESIGN | [18 empty] | ENGINEERING DESIGN DETAIL |  | PROCUREMENT
REVISION | P&ID DRAWING | TAG No. | FUNCTIONAL LOCATION | EQUIPMENT TYPE | EQUIPMENT DESCRIPTION | STATUS | POWER (kW) | VOLTAGE (V) | SIZE | DESIGN PRESSURE (KPA) | DI | AI | DO | AO | INPUT | OUTPUT | RANGE | SCALE | MAKE | MODEL | SERIAL No. | SUPPLIER | INSTALLED BY | DATASHEET | COMMENTS
B | GT36-060-83.4 | FSH83401 | Ancillaries | Flow Switch High | Shower in use indicator SSE83401 | [5 empty] | 1 | [6 empty] | L/min | Kelco or equivalent | [5 empty] | 25mm BSP Thread
B | GT36-060-83.4 | FSH83402 | Ancillaries | Flow Switch High | Shower in use indicator SSE83402 | [5 empty] | 1 | [6 empty] | L/min | Kelco or equivalent | [5 empty] | 25mm BSP Thread
B | GT36-060-83.4 | FSH83403 | Ancillaries | Flow Switch High | Shower in use indicator SSE83403 | [5 empty] | 1 | [6 empty] | L/min | Kelco or equivalent | [5 empty] | 25mm BSP Thread
B | GT36-060-83.4 | FSL83410 | Ancillaries | Flow Switch Low | Treated Sample Water Low Flow Switch | [5 empty] | 1 | [6 empty] | L/min | Kelco or equivalent | [5 empty] | 15mm PVC spigots
B | GT36-060-83.4 | AE83411 | Ancillaries | Analysis Element | Fluoride Analysis Element
B | GT36-060-83.4 | AIT83411 | Ancillaries | Analysis Indicating Transmitter | Fluoride Indicating Transmitter | [6 empty] | 1 |  |  |  |  | 0 - 2 | ppm | Prominent
B | GT36-060-83.4 | FI83412 | Ancillaries | Variable Area Flow Indicator | Treated Sample Water Variable Area Flow Indicator
B | GT36-060-83.4 | LS83303(HH) | Ancillaries | Level Switch High High | Analysis Sample Return Water Tank High High Level Switch
B | GT36-060-83.4 | LS83303(H) | Ancillaries | Level Switch High | Analysis Sample Return Water Tank High Level Switch
B | GT36-060-83.4 | LS83303(L) | Ancillaries | Level Switch Low | Analysis Sample Return Water Tank Low Level Switch
B | GT36-060-83.4 | NZ83303 | Ancillaries | Torque Actuator | Sample Pump Return Water Torque Actuator

## Mechanical
MECHANICAL SCHEDULE - FLUROSILICIC ACID: OVERALL
ENGINEERING DESIGN | [14 empty] | ENGINEERING DESIGN DETAIL |  |  |  | PROCUREMENT
REVISION | P&ID DRAWING | TAG No. | FUNCTIONAL LOCATION | EQUIPMENT TYPE | EQUIPMENT DESCRIPTION | STATUS | POWER (kW) | VOLTAGE (V) | SIZE | DESIGN PRESSURE (KPA) | INPUT | OUTPUT | RANGE | SCALE | MAKE | MODEL | END CONNECTION TYPE | END CONNECTION STANDARD | SERIAL No. | SUPPLIER | INSTALLED BY | DATASHEET | COMMENTS
D | GT36-060-83.1 | FN83101 | FSA Storage Room | Fan | FSA Storage Exhaust Fans |  |  | 240 | [14 empty] | Wall Mounted. Refer to DS70-01
D | GT36-060-83.1 | TA83110 | FSA Storage Room | Tank | FSA Storage Tank #1 |  | N/A | N/A | [6 empty] | GRP Technology or GFR Industries or Fusion Pty Ltd |  | Flanged | AS2129 Table 'E' |  |  |  |  | Capacity: _______m³ (Net). Construction: GRP or HDPE. Refer to tank nozzle layout drawings
D | GT36-060-83.1 | TA83120 | FSA Storage Room | Tank | FSA Storage Tank #2 |  | N/A | N/A | [6 empty] | GRP Technology or GFR Industries or Fusion Pty Ltd |  | Flanged | AS2129 Table 'E' |  |  |  |  | Capacity: _______m³ (Net). Construction: GRP or HDPE. Refer to tank nozzle layout drawings
D | GT36-060-83.1 | RPZ83102 | FSA Storage Room | Residual Pressure Device | Optional RPZD Refer to Note 4 |  | N/A | N/A | 50 | 800kPa |  |  |  |  | RMC or Febco
MECHANICAL SCHEDULE - FLUROSILICIC ACID: DOSING PANEL 1
ENGINEERING DESIGN | [14 empty] | ENGINEERING DESIGN DETAIL |  |  |  | PROCUREMENT
REVISION | P&ID DRAWING | TAG No. | FUNCTIONAL LOCATION | EQUIPMENT TYPE | EQUIPMENT DESCRIPTION | STATUS | POWER (kW) | VOLTAGE (V) | SIZE | DESIGN PRESSURE (KPA) | INPUT | OUTPUT | RANGE | SCALE | MAKE | MODEL | END CONNECTION TYPE | END CONNECTION STANDARD | SERIAL No. | SUPPLIER | INSTALLED BY | DATASHEET | COMMENTS
B | GT36-060-83.2 | CC83208 | Dosing Panel 1 | Calibration Column | Calibration Column |  | N/A | N/A | [6 empty] | Koflo or equivalent |  | Threaded | NPT |  |  |  |  | 1000ml tube with 5 ml intervals. All PVC (No Glass)
B | GT36-060-83.2 | ST83211 | Dosing Panel 1 | Strainer | Dosing Pump Suction Strainer |  | N/A | N/A | [6 empty] | George Fischer or equivalent |  | Solvent cement spigot with union end | N/A |  |  |  |  | DN15 Y body PVC line strainer Cylindrical screen with perforations 0.5mm
B | GT36-060-83.2 | PU83213 | Dosing Panel 1 | Pump | Dosing Pump |  | 0.2 | 415 |  | Internal Pressure Relief: set to pump head rating ~ 700kPa |  |  |  |  | Iwaki or Wallace & Tiernan | Profibus DP Interface | Flanged | AS2129 Table 'E' |  |  |  |  | Duty: _____L/h @ ____kPa. Construction: Hydraulic Diaphragm, PVC Head & PTFE Diaphragm. Supplied c/w manual Stroke Adjustment & Movimot variable speed motor and controller
B | GT36-060-83.2 | PD83215 | Dosing Panel 1 | Pulsation Dampener | Pulsation Dampener Dosing Panel |  | N/A | N/A | [6 empty] | Accu-pulse or equivalent. (Usually supplied as part of dosing pump package) |  | Threaded | BSP |  |  |  |  | Duty: Minimum 26 x pump stroke volume & 95% dampening Construction: Body - PVC, Bladder - Hypalon or suitable for FSA. Supplied c/w pressure indicator & compressed air connection
B | GT36-060-83.2 | TA83230 | Dosing Panel 1 | Tank | Flushing Container |  | N/A | N/A | 10L Dangerous Goods Approved (DGA) Polyethylene cube. Length - 220mm, Width - 220mm & Height - 310mm. | [5 empty] | Silverlock |  | 50mm threaded cap | N/A |  |  |  |  | Translucent white - DG Blank (no bung provision) or DG WBNH (with bung no hole).
MECHANICAL SCHEDULE - FLUROSILICIC ACID: DOSING PANEL 2
ENGINEERING DESIGN | [14 empty] | ENGINEERING DESIGN DETAIL |  |  |  | PROCUREMENT
REVISION | P&ID DRAWING | TAG No. | FUNCTIONAL LOCATION | EQUIPMENT TYPE | EQUIPMENT DESCRIPTION | STATUS | POWER (kW) | VOLTAGE (V) | SIZE | DESIGN PRESSURE (KPA) | INPUT | OUTPUT | RANGE | SCALE | MAKE | MODEL | END CONNECTION TYPE | END CONNECTION STANDARD | SERIAL No. | SUPPLIER | INSTALLED BY | DATASHEET | COMMENTS
B | GT36-060-83.3 | CC83308 | Dosing Panel 2 | Calibration Column | Calibration Column |  | N/A | N/A | [6 empty] | Koflo or equivalent |  | Threaded | NPT |  |  |  |  | 1000ml tube with 5 ml intervals. All PVC (No Glass)
B | GT36-060-83.3 | ST83311 | Dosing Panel 2 | Strainer | Dosing Pump Suction Strainer |  | N/A | N/A | [6 empty] | George Fischer or equivalent |  | Solvent cement spigot with union end | N/A |  |  |  |  | DN15 Y body PVC line strainer Cylindrical screen with perforations 0.5mm
B | GT36-060-83.3 | PU83313 | Dosing Panel 2 | Pump | Dosing Pump |  | 0.2 | 415 |  | Internal Pressure Relief: set to pump head rating ~ 700kPa |  |  |  |  | Iwaki or Wallace & Tiernan | Profibus DP Interface | Flanged | AS2129 Table 'E' |  |  |  |  | Duty: _____L/h @ ____kPa. Construction: Hydraulic Diaphragm, PVC Head & PTFE Diaphragm. Supplied c/w manual Stroke Adjustment & Movimot variable speed motor and controller
B | GT36-060-83.3 | PD83315 | Dosing Panel 2 | Pulsation Dampener | Pulsation Dampener Dosing Panel |  | N/A | N/A | [6 empty] | Accu-pulse or equivalent. (Usually supplied as part of dosing pump package) |  | Threaded | BSP |  |  |  |  | Duty: Minimum 26 x pump stroke volume & 95% dampening Construction: Body - PVC, Bladder - Hypalon or suitable for FSA. Supplied c/w pressure indicator & compressed air connection
B | GT36-060-83.3 | TA83330 | Dosing Panel 2 | Tank | Flushing Container |  | N/A | N/A | 10L Dangerous Goods Approved (DGA) Polyethylene cube. Length - 220mm, Width - 220mm & Height - 310mm. | [5 empty] | Silverlock |  | 50mm threaded cap | N/A |  |  |  |  | Translucent white - DG Blank (no bung provision) or DG WBNH (with bung no hole).
MECHANICAL SCHEDULE - FLUROSILICIC ACID: ANCILLARIES
ENGINEERING DESIGN | [14 empty] | ENGINEERING DESIGN DETAIL |  |  |  | PROCUREMENT
REVISION | P&ID DRAWING | TAG No. | FUNCTIONAL LOCATION | EQUIPMENT TYPE | EQUIPMENT DESCRIPTION | STATUS | POWER (kW) | VOLTAGE (V) | SIZE | DESIGN PRESSURE (KPA) | INPUT | OUTPUT | RANGE | SCALE | MAKE | MODEL | END CONNECTION TYPE | END CONNECTION STANDARD | SERIAL No. | SUPPLIER | INSTALLED BY | DATASHEET | COMMENTS
B | GT36-060-83.4 | SSE83401 | Ancillaries | Safety Shower and Eyewash | Dosing Panel Area |  | N/A | N/A | [6 empty] | Ashley Safety or equivalent |  | Threaded | BSP |  |  |  |  | Combination Safety Shower and Eye Wash Station c/w Flow Switch Refer DS79-02
B | GT36-060-83.4 | SSE83402 | Ancillaries | Safety Shower and Eyewash | Load-in Panel Area |  | N/A | N/A | [6 empty] | Ashley Safety or equivalent |  | Threaded | BSP |  |  |  |  | Combination Safety Shower and Eye Wash Station c/w Flow Switch Refer DS79-02
B | GT36-060-83.4 | SSE83403 | Ancillaries | Safety Shower and Eyewash | Load-in Apron Area |  | N/A | N/A | [6 empty] | Ashley Safety or equivalent |  | Threaded | BSP |  |  |  |  | Combination Safety Shower and Eye Wash Station c/w Flow Switch Refer DS79-02
B | GT36-060-83.4 | RWH83404 | Ancillaries | Retractable Washdown Hose | Dosing Panel Area |  | N/A | N/A | [6 empty] | Chubb or equivalent |  | Threaded | BSP |  |  |  |  | Diameter: 19mm or larger Hose length: 20m or longer
B | GT36-060-83.4 | RWH83405 | Ancillaries | Retractable Washdown Hose | Outdoor Load-in Panel Area |  | N/A | N/A | [6 empty] | Chubb or equivalent |  | Threaded | BSP |  |  |  |  | Diameter: 19mm or larger Hose length: 20m or longer
B | GT36-060-83.4 | TA83403 | Ancillaries | Tank | Analyser Sample Return Water Tank
B | GT36-060-83.4 | PU83403 | Ancillaries | Pump | Sample Water Return Pump
B | GT36-060-83.4 | FR83401 | Ancillaries | Filter | Filter

## Valve
VALVE SCHEDULE - FLUROSILICIC ACID: OVERALL
ENGINEERING DESIGN | [14 empty] | ENGINEERING DESIGN DETAIL |  |  |  | PROCUREMENT
REVISION | P&ID DRAWING | TAG No. | FUNCTIONAL LOCATION | EQUIPMENT TYPE | EQUIPMENT DESCRIPTION | STATUS | POWER (kW) | VOLTAGE (V) | SIZE | DESIGN PRESSURE (KPA) | INPUT | OUTPUT | RANGE | SCALE | MAKE | MODEL | END CONNECTION TYPE | END CONNECTION STANDARD | SERIAL No. | SUPPLIER | INSTALLED BY | DATASHEET | COMMENTS
D | GT36-060-83.1 | VA83101 | FSA Storage Room | Ball Valve | Site Service Water Isolation Valve | Service Water |  |  | 50 | 800kPa |  |  |  |  | George Fischer |  | Solvent cement socket | N/A |  |  |  |  | This valve may not need to be pvc if it is located outside the bunded area.
D | GT36-060-83.1 | VA83103 | FSA Storage Room | Ball Valve | Service Water Safety Shower Isolation Valve | Service Water |  |  | 32 | 800kPa |  |  |  |  | George Fischer |  | Solvent cement socket | N/A |  |  |  |  | All PVC construction
D | GT36-060-83.1 | VA83104 | FSA Storage Room | Ball Valve | Internal Bund Sump Float Isolation Valve | Service Water |  |  | 25 | 800kPa |  |  |  |  | George Fischer |  | Solvent cement socket | N/A |  |  |  |  | All PVC construction
D | GT36-060-83.1 | VA83105 | FSA Storage Room | Float Valve | Internal Bund Sump Float Valve | Service Water |  |  | 25 | 800kPa |  |  |  |  | George Fischer |  | Threaded | BSP |  |  |  |  | Float Operated Valve to maintain constant water level in sump All PE construction.
D | GT36-060-83.1 | VA83106 | FSA Storage Room | Ball Valve | Load-in Panel Drain to Bund Sump Valve | FSA/ Service Water/ Waste |  |  | 50 | 600kPa |  |  |  |  | George Fischer |  | Solvent cement socket | N/A |  |  |  |  | All PVC construction
D | GT36-060-83.1 | VA83107 | FSA Storage Room | Ball Valve | Internal Bund Sump Non-return Isolation Valve | FSA/ Service Water/ Waste |  |  | 50 | 800kPa |  |  |  |  | George Fischer |  | Solvent cement socket | N/A |  |  |  |  | All PVC construction
D | GT36-060-83.1 | VA83108 | FSA Storage Room | Non-return Valve | Internal Bund Sump Non-return Valve | FSA/ Service Water/ Waste |  |  | 50 | 800kPa |  |  |  |  | George Fischer |  | Solvent cement socket | N/A |  |  |  |  | All PVC construction
D | GT36-060-83.1 | VA83109 | FSA Storage Room | Ball Valve | Sump/ Tank Pump out Isolation Valve | FSA/ Service Water/ Waste |  |  | 50 | 800kPa |  |  |  |  | George Fischer |  | Solvent cement socket | N/A |  |  |  |  | All PVC construction
D | GT36-060-83.1 | VA83110 | FSA Storage Room | Ball Valve | Load-in Panel to Tank 1 Isolation Valve | FSA |  |  | 50 | 600kPa |  |  |  |  | George Fischer |  | Solvent cement socket | N/A |  |  |  |  | All PVC construction
D | GT36-060-83.1 | VA83111 | FSA Storage Room | 3-way Valve | LI83110 level indicator tank isolation valve | FSA |  |  | 50 | 600kPa | 3/4" flanged or NPT inlet/outlet on magnetic level gauge (Ekotech - model 048 mini) |  |  |  | George Fischer |  | Flanged Socket | N/A |  |  |  |  | All PVC construction
D | GT36-060-83.1 | VA83112 | FSA Storage Room | Ball Valve | LI83110 level indicator isolation valve | FSA |  |  | 20 | 600kPa | 3/4" flanged or NPT inlet/outlet on magnetic level gauge (Ekotech - model 048 mini) |  |  |  | George Fischer |  | Solvent cement socket | N/A |  |  |  |  | All PVC construction
D | GT36-060-83.1 | VA83113 | FSA Storage Room | Ball Valve | LT83113 pressure transmitter isolation valve | FSA |  |  | 15 | 600kPa |  |  |  |  | George Fischer |  | Solvent cement socket | N/A |  |  |  |  | All PVC construction 1/2" threaded process connection on pressure transmitter, will also need diaphragm.
D | GT36-060-83.1 | VA83114 | FSA Storage Room | Ball Valve | Scour Valve | FSA |  |  | 50 | 600kPa |  |  |  |  | George Fischer |  | Flanged Socket | N/A |  |  |  |  | All PVC construction
D | GT36-060-83.1 | VA83115 | FSA Storage Room | Ball Valve | Tank 1 level instruments tank isolation valve | FSA |  |  | 50 | 600kPa |  |  |  |  | George Fischer |  | Flanged Socket | N/A |  |  |  |  | All PVC construction
D | GT36-060-83.1 | VA83116 | FSA Storage Room | Ball Valve | Tank 1 Manual Isolation Valve | FSA |  |  | 50 | 600kPa |  |  |  |  | George Fischer |  | Flanged Socket | N/A |  |  |  |  | Requires stub flange to be mounted directly on tank nozzle flange. Needs to have open/close position clearly marked. All PVC construction
D | GT36-060-83.1 | VA83117 | FSA Storage Room | Motorised Valve | Motorised Outlet Valve | FSA |  | 24V DC 2 SPDT Limit switches | 50 | 600kPa |  |  |  |  | George Fischer |  | Solvent cement socket | N/A |  |  |  |  | All PVC construction
D | GT36-060-83.1 | VA83118 | FSA Storage Room | Motorised 3-way Valve | 3-way Motorised FSA Panel Supply/ Service Water | FSA/ Service Water |  | 24V DC 2 SPDT Limit switches | 50 | 800kPa |  |  |  |  | George Fischer |  | Solvent cement socket | N/A |  |  |  |  | All PVC construction
D | GT36-060-83.1 | VA83120 | FSA Storage Room | Ball Valve | Load-in Panel to Tank 2 Isolation Valve | FSA |  |  | 50 | 600kPa |  |  |  |  | George Fischer |  | Solvent cement socket | N/A |  |  |  |  | All PVC construction
D | GT36-060-83.1 | VA83121 | FSA Storage Room | 3-way Valve | LI83120 level indicator tank isolation valve | FSA |  |  | 50 | 600kPa | 3/4" flanged or NPT inlet/outlet on magnetic level gauge (Ekotech - model 048 mini) |  |  |  | George Fischer |  | Flanged Socket | N/A |  |  |  |  | All PVC construction
D | GT36-060-83.1 | VA83122 | FSA Storage Room | Ball Valve | LI83120 level indicator isolation valve | FSA |  |  | 20 | 600kPa | 3/4" flanged or NPT inlet/outlet on magnetic level gauge (Ekotech - model 048 mini) |  |  |  | George Fischer |  | Solvent cement socket | N/A |  |  |  |  | All PVC construction
D | GT36-060-83.1 | VA83123 | FSA Storage Room | Ball Valve | LT83123 pressure transmitter isolation valve | FSA |  |  | 15 | 600kPa |  |  |  |  | George Fischer |  | Solvent cement socket | N/A |  |  |  |  | All PVC construction 1/2" threaded process connection on pressure transmitter, will also need diaphragm.
D | GT36-060-83.1 | VA83124 | FSA Storage Room | Ball Valve | Scour Valve | FSA |  |  | 50 | 600kPa |  |  |  |  | George Fischer |  | Flanged Socket | N/A |  |  |  |  | All PVC construction
D | GT36-060-83.1 | VA83125 | FSA Storage Room | Ball Valve | Level instrument isolation valve | FSA |  |  | 50 | 600kPa |  |  |  |  | George Fischer |  | Flanged Socket | N/A |  |  |  |  | All PVC construction
D | GT36-060-83.1 | VA83126 | FSA Storage Room | Ball Valve | Tank 2 Manual Isolation Valve | FSA |  |  | 50 | 600kPa |  |  |  |  | George Fischer |  | Flanged Socket | N/A |  |  |  |  | Requires stub flange to be mounted directly on tank nozzle flange. Needs to have open/close position clearly marked. All PVC construction
D | GT36-060-83.1 | VA83127 | FSA Storage Room | Motorised Valve | Motorised Outlet Valve | FSA |  | 24V DC 2 SPDT Limit switches | 50 | 600kPa |  |  |  |  | George Fischer |  | Solvent cement socket | N/A |  |  |  |  | All PVC construction
D | GT36-060-83.1 | VA83128 | FSA Storage Room | Motorised 3-way Valve | 3-way Motorised FSA Panel Supply/ Service Water | FSA/ Service Water |  | 24V DC 2 SPDT Limit switches | 50 | 800kPa |  |  |  |  | George Fischer |  | Solvent cement socket | N/A |  |  |  |  | All PVC construction
D | GT36-060-83.1 | VA83130 | FSA Storage Room | Ball Valve | Load in panel, load in drain Valve | FSA |  |  | 15 | 800kPa |  |  |  |  | George Fischer |  | Solvent cement socket | N/A |  |  |  |  | All PVC construction
D | GT36-060-83.1 | VA83131 | FSA Storage Room | Non-return Valve | Site Service Water to Tank 1 FSA Non-return Valve | Service Water |  |  | 25 | 800kPa |  |  |  |  | George Fischer |  | Solvent cement socket | N/A |  |  |  |  | Needs to be mounted in vertical position All PVC construction Valve is normally closed (Spring to close)
D | GT36-060-83.1 | VA83132 | FSA Storage Room | Motorised Valve | Site Service Water to Tank 1 FSA Motorised Valve | Service Water |  | 24V DC 2 SPDT Limit switches | 25 | 800kPa |  |  |  |  | George Fischer |  | Solvent cement socket | N/A |  |  |  |  | All PVC construction
D | GT36-060-83.1 | VA83133 | FSA Storage Room | Non-return Valve | Site Service Water to Tank 2 FSA Non-return Valve | Service Water |  |  | 25 | 800kPa |  |  |  |  | George Fischer |  | Solvent cement socket | N/A |  |  |  |  | Needs to be mounted in vertical position
D | GT36-060-83.1 | VA83134 | FSA Storage Room | Motorised Valve | Site Service Water to Tank 2 FSA Motorised Valve | Service Water |  |  | 25 | 800kPa |  |  |  |  | George Fischer |  | Solvent cement socket | N/A |  |  |  |  | Needs to be mounted in vertical position All PVC construction
D | GT36-060-83.1 | VA83135 | FSA Storage Room | Ball Valve | Main line Flushing Isolation Valve | Service Water |  |  | 50 | 600kPa |  |  |  |  | George Fischer |  | Solvent cement socket | N/A |  |  |  |  | All PVC construction
D | GT36-060-83.1 | VA83136 | FSA Storage Room | Ball Valve | Main line Flushing Isolation Valve | Service Water |  |  | 50 | 600kPa |  |  |  |  | George Fischer |  | Solvent cement socket | N/A |  |  |  |  | All PVC construction
D | GT36-060-83.1 | VA83137 | FSA Storage Room | Motorised 3-way Valve | Valve Pit Motorised 3-way Valve | FSA/Service Water/Waste |  | 24V DC 2 SPDT Limit Switches 24 VDC, Actuator mounted on extension spindle - 700mm long | 50 | 100kPa |  |  |  |  | George Fischer |  | Solvent cement socket | N/A |  |  |  |  | Electric actuator to be mounted above sump. All PVC construction
D | GT36-060-83.1 | VA83138 | FSA Storage Room | Motorised 3-way Valve | Load-in Apron sump Motorised 3-way Valve | FSA/ Rainwater |  | 24V DC 2 SPDT Limit Switches 24 VDC, Actuator mounted on extension spindle - 700mm long | 50 | 100kPa |  |  |  |  | George Fischer |  | Solvent cement socket | N/A |  |  |  |  | All PVC construction
D | GT36-060-83.1 | VA83140 | FSA Storage Room | Ball Valve | Valve Pit Manual Valve | FSA/Service Water/Waste |  |  | 50 | 100kPa |  |  |  |  | George Fischer |  | Solvent cement socket | N/A |  |  |  |  | All PVC construction
D | GT36-060-83.1 | VA83142 | FSA Storage Room | Non-return Valve | Waste Holding Tank Non-return Valve | FSA/Service Water/Waste |  |  | 50 | 800kPa |  |  |  |  | George Fischer |  | Solvent cement socket | N/A |  |  |  |  | Ball check valve and 050 screen combined for foot valve configuration. All PVC Construction.
D | GT36-060-83.1 | VA83143 | FSA Storage Room | Ball Valve | Waste Holding Tank Isolation Valve | FSA/Service Water/Waste |  |  | 50 | 800kPa |  |  |  |  | George Fischer |  | Solvent cement socket | N/A |  |  |  |  | All PVC construction
D | GT36-060-83.1 | VA83145 | FSA Storage Room | Ball Valve | Tank 1 Flushing Connection Isolation Valve | Service Water |  |  | 20 | 800kPa |  |  |  |  | George Fischer |  | Solvent cement socket | N/A |  |  |  |  | All PVC construction
D | GT36-060-83.1 | VA83146 | FSA Storage Room | Ball Valve | LI83110 level indicator drain valve | FSA/Service Water/Waste |  |  | 20 | 800kPa |  |  |  |  | George Fischer |  | Solvent cement socket | N/A |  |  |  |  | All PVC construction
D | GT36-060-83.1 | VA83147 | FSA Storage Room | Ball Valve | LT83113 pressure transmitter drain valve | FSA/Service Water/Waste |  |  | 20 | 800kPa |  |  |  |  | George Fischer |  | Solvent cement socket | N/A |  |  |  |  | All PVC construction
D | GT36-060-83.1 | VA83148 | FSA Storage Room | Ball Valve | Tank 1 Flushing Connection Isolation Valve | Service Water |  |  | 20 | 800kPa |  |  |  |  | George Fischer |  | Solvent cement socket | N/A |  |  |  |  | All PVC construction
D | GT36-060-83.1 | VA83149 | FSA Storage Room | Ball Valve | Tank 1 Drain Valve | FSA/Service Water/Waste |  | Handle extension - 700mm long | 15 | 800kPa |  |  |  |  | George Fischer |  | Solvent cement socket | N/A |  |  |  |  | All PVC construction
D | GT36-060-83.1 | VA83151 | FSA Storage Room | Ball Valve | Tank 2 Flushing Connection Isolation Valve | Service Water |  |  | 20 | 800kPa |  |  |  |  | George Fischer |  | Solvent cement socket | N/A |  |  |  |  | All PVC construction
D | GT36-060-83.1 | VA83152 | FSA Storage Room | Ball Valve | LI83120 level indicator drain valve | FSA/ Service Water |  |  | 20 | 800kPa |  |  |  |  | George Fischer |  | Solvent cement socket | N/A |  |  |  |  | All PVC construction
D | GT36-060-83.1 | VA83153 | FSA Storage Room | Ball Valve | LT83123 pressure transmitter drain valve | FSA/ Service Water |  |  | 20 | 800kPa |  |  |  |  | George Fischer |  | Solvent cement socket | N/A |  |  |  |  | All PVC construction
D | GT36-060-83.1 | VA83154 | FSA Storage Room | Ball Valve | Tank 2 Flushing Connection Isolation Valve | Service Water |  |  | 20 | 800kPa |  |  |  |  | George Fischer |  | Solvent cement socket | N/A |  |  |  |  | All PVC construction
D | GT36-060-83.1 | VA83155 | FSA Storage Room | Ball Valve | Tank 2 Drain Valve | FSA/ Service Water |  |  | 15 | [5 empty] | George Fischer |  | Solvent cement socket | N/A |  |  |  |  | Valve handle to be lockable. To be located at lowest point between tank and panel closest to tank. Purpose to be signposted.
VALVE SCHEDULE - FLUROSILICIC ACID: DOSING PANEL 1
ENGINEERING DESIGN | [14 empty] | ENGINEERING DESIGN DETAIL |  |  |  | PROCUREMENT
REVISION | P&ID DRAWING | TAG No. | FUNCTIONAL LOCATION | EQUIPMENT TYPE | EQUIPMENT DESCRIPTION | STATUS | POWER (kW) | VOLTAGE (V) | SIZE | DESIGN PRESSURE (KPA) | INPUT | OUTPUT | RANGE | SCALE | MAKE | MODEL | END CONNECTION TYPE | END CONNECTION STANDARD | SERIAL No. | SUPPLIER | INSTALLED BY | DATASHEET | COMMENTS
B | GT36-060-83.2 | VA83201 | Dosing Panel 1 | Ball Valve | Dilution Water Supply Isolation Valve | Chlorine Solution, Service Water or Sample Water |  |  | 25 | 800kPa |  |  |  |  | George Fischer |  | Solvent cement socket | N/A |  |  |  |  | All PVC construction
B | GT36-060-83.2 | VA83202 | Dosing Panel 1 | Motorised Valve | Dilution Water Supply Actuated Valve | Chlorine Solution, Service Water or Sample Water |  | 24V DC 2 SPDT Limit Switches | 25 | 800kPa |  |  |  |  | George Fischer |  | Solvent cement socket | N/A |  |  |  |  | All PVC construction
B | GT36-060-83.2 | VA83203 | Dosing Panel 1 | Pressure Reducing Internal Valve | Dilution Water Supply PRV | Chlorine Solution, Service Water or Sample Water |  |  | 25
B | GT36-060-83.2 | VA83204 | Dosing Panel 1 | Ball Valve | Pressure Indicator Isolation Valve | Chlorine Solution, Service Water or Sample Water |  |  | 15 | 800kPa |  |  |  |  | George Fischer |  | Solvent cement socket | N/A |  |  |  |  | All PVC construction
B | GT36-060-83.2 | VA83206 | Dosing Panel 1 | Ball Valve | Service Water Isolation Valve | Service Water |  |  | 15 | 800kPa |  |  |  |  | George Fischer |  | Solvent cement socket | N/A |  |  |  |  | All PVC construction
B | GT36-060-83.2 | VA83207 | Dosing Panel 1 | Non-return Valve | Calibration Column Non-return valve | Service Water |  |  | 15 | 800kPa |  |  |  |  | George Fischer |  | Solvent cement socket | N/A |  |  |  |  | All PVC construction. Typ 360 complete with polypyrene s.g. = 0.09 (special) - so it floats
B | GT36-060-83.2 | VA83208 | Dosing Panel 1 | Ball Valve | Calibration Column Isolation Valve | Service Water |  |  | 15 | 800kPa |  |  |  |  | George Fischer |  | Solvent cement socket | N/A |  |  |  |  | All PVC construction
B | GT36-060-83.2 | VA83209 | Dosing Panel 1 | Ball Valve | FSA Supply from Tank 1 Isolation Valve | FSA |  |  | 15 | 800kPa |  |  |  |  | George Fischer |  | Solvent cement socket | N/A |  |  |  |  | All PVC construction
B | GT36-060-83.2 | VA83210 | Dosing Panel 1 | 3-way Valve | Service Water/ FSA Supply Water 3 way valve | FSA |  |  | 15 | 800kPa |  |  |  |  | George Fischer |  | Solvent cement socket | N/A |  |  |  |  | All PVC construction
B | GT36-060-83.2 | VA83212 | Dosing Panel 1 | Ball Valve | Pump Suction Isolation Valve | FSA |  |  | 15 | 800kPa |  |  |  |  | George Fischer |  | Solvent cement socket | N/A |  |  |  |  | All PVC construction
B | GT36-060-83.2 | VA83213 | Dosing Panel 1 | Relief Angle Valve | Pump Relief Valve | FSA |  |  | 15 | 1000kPa |  |  |  |  | George Fischer |  | Solvent cement socket union | N/A |  |  |  |  | Pressure Setpoint: below lowest pressure rating of fittings/ equipment in downstream pipework, above pump max duty pressure but below pump IRV eg 600kPa. All PVC Construction. Adjustable Spring loaded
B | GT36-060-83.2 | VA83214 | Dosing Panel 1 | Ball Valve | Pump Discharge Isolation Valve | FSA |  |  | 15 | 800kPa |  |  |  |  | George Fischer |  | Solvent cement socket | N/A |  |  |  |  | All PVC construction
B | GT36-060-83.2 | VA83215 | Dosing Panel 1 | Ball Valve | Pulsation Dampener Isolation Valve | FSA |  |  | 15 | 800kPa |  |  |  |  | George Fischer |  | Solvent cement socket | N/A |  |  |  |  | All PVC construction
B | GT36-060-83.2 | VA83216 | Dosing Panel 1 | Ball Valve | Pressure Indicator Isolation Valve | FSA |  |  | 15 | 800kPa |  |  |  |  | George Fischer |  | Solvent cement socket | N/A |  |  |  |  | All PVC construction
B | GT36-060-83.2 | VA83217 | Dosing Panel 1 | Ball Valve | Magflow Inlet Isolation Valve | FSA |  |  | 15 | 800kPa |  |  |  |  | George Fischer |  | Solvent cement socket | N/A |  |  |  |  | All PVC construction
B | GT36-060-83.2 | VA83219 | Dosing Panel 1 | Pressure Sustaining Valve | Magflow PSV | FSA |  |  | 15 | 1000kPa |  |  |  |  | George Fischer |  | Solvent cement socket union | N/A |  |  |  |  | Pressure Setpoint: dose point back pressure + 200kPa eg 500kPa; All PVC Construction. Adjustable Spring loaded
B | GT36-060-83.2 | VA83220 | Dosing Panel 1 | Ball Valve | Magflow Outlet Isolation Valve | FSA |  |  | 15 | 800kPa |  |  |  |  | George Fischer |  | Solvent cement socket | N/A |  |  |  |  | All PVC construction
B | GT36-060-83.2 | VA83221 | Dosing Panel 1 | Ball Valve | Magflow Bypass Valve | FSA |  |  | 15 | 800kPa |  |  |  |  | George Fischer |  | Solvent cement socket | N/A |  |  |  |  | All PVC construction
B | GT36-060-83.2 | VA83222 | Dosing Panel 1 | Ball Valve | Air Vent Isolation Valve | FSA/ Air |  |  | 15 | 800kPa |  |  |  |  | George Fischer |  | Solvent cement socket | N/A |  |  |  |  | All PVC construction
B | GT36-060-83.2 | VA83223 | Dosing Panel 1 | Auto Air Vent Valve | Air Vent Valve | FSA/ Air |  |  | 15 | 800kPa |  |  |  |  | Stubbe or Equivalent |  | Solvent cement socket | N/A |  |  |  |  | All PVC construction Needs to be mounted vertically
B | GT36-060-83.2 | VA83224 | Dosing Panel 1 | Motorised 3-way Valve | FSA Supply/ Drip Tray Actuated 3-way Valve | FSA |  | 24V DC 2 SPDT Limit Switches | 15 | 800kPa |  |  |  |  | George Fischer |  | Solvent cement socket | N/A |  |  |  |  | All PVC construction Specifically T or L port
B | GT36-060-83.2 | VA83225 | Dosing Panel 1 | Ball Valve | FSA Supply/ Dose Point Isolation Valve | FSA |  |  | 15 | 800kPa |  |  |  |  | George Fischer |  | Solvent cement socket | N/A |  |  |  |  | All PVC construction
B | GT36-060-83.2 | VA83226 | Dosing Panel 1 | Non-return Valve | FSA Supply Non-return Valve | FSA |  |  | 15 | 800kPa |  |  |  |  | George Fischer |  | Solvent cement socket | N/A |  |  |  |  | All PVC construction
B | GT36-060-83.2 | VA83227 | Dosing Panel 1 | Ball Valve | Dilution Water Supply Isolation Valve | Chlorine Solution, Service Water or Sample Water |  |  | 25 | 800kPa |  |  |  |  | George Fischer |  | Solvent cement socket | N/A |  |  |  |  | All PVC construction
B | GT36-060-83.2 | VA83228 | Dosing Panel 1 | Non-return Valve | Dilution Water Supply Non-return Valve | Chlorine Solution, Service Water or Sample Water |  |  | 25 | 800kPa |  |  |  |  | George Fischer |  | Solvent cement socket | N/A |  |  |  |  | All PVC construction
B | GT36-060-83.2 | VA83229 | Dosing Panel 1 | Ball Valve | Dosing Panel 1 Isolation to Dose Point | Chlorine Solution, Service Water or Sample Water |  |  | 25 | 800kPa |  |  |  |  | George Fischer |  | Solvent cement socket | N/A |  |  |  |  | All PVC construction
VALVE SCHEDULE - FLUROSILICIC ACID: DOSING PANEL 2
ENGINEERING DESIGN | [14 empty] | ENGINEERING DESIGN DETAIL |  |  |  | PROCUREMENT
REVISION | P&ID DRAWING | TAG No. | FUNCTIONAL LOCATION | EQUIPMENT TYPE | EQUIPMENT DESCRIPTION | STATUS | POWER (kW) | VOLTAGE (V) | SIZE | DESIGN PRESSURE (KPA) | INPUT | OUTPUT | RANGE | SCALE | MAKE | MODEL | END CONNECTION TYPE | END CONNECTION STANDARD | SERIAL No. | SUPPLIER | INSTALLED BY | DATASHEET | COMMENTS
B | GT36-060-83.3 | VA83301 | Dosing Panel 2 | Ball Valve | Dilution Water Supply Isolation Valve | Chlorine Solution, Service Water or Sample Water |  |  | 25 | 800kPa |  |  |  |  | George Fischer |  | Solvent cement socket | N/A |  |  |  |  | All PVC construction
B | GT36-060-83.3 | VA83302 | Dosing Panel 2 | Motorised Valve | Dilution Water Supply Actuated Valve | Chlorine Solution, Service Water or Sample Water |  | 24V DC 2 SPDT Limit Switches | 25 | 800kPa |  |  |  |  | George Fischer |  | Solvent cement socket | N/A |  |  |  |  | All PVC construction
B | GT36-060-83.3 | VA83303 | Dosing Panel 2 | Pressure Reducing Internal Valve | Dilution Water Supply PRV | Chlorine Solution, Service Water or Sample Water |  |  | 25
B | GT36-060-83.3 | VA83304 | Dosing Panel 2 | Ball Valve | Pressure Indicator Isolation Valve | Chlorine Solution, Service Water or Sample Water |  |  | 15 | 800kPa |  |  |  |  | George Fischer |  | Solvent cement socket | N/A |  |  |  |  | All PVC construction
B | GT36-060-83.3 | VA83306 | Dosing Panel 2 | Ball Valve | Service Water Isolation Valve | Service Water |  |  | 15 | 800kPa |  |  |  |  | George Fischer |  | Solvent cement socket | N/A |  |  |  |  | All PVC construction
B | GT36-060-83.3 | VA83307 | Dosing Panel 2 | Non-return Valve | Calibration Column Non-return valve | Service Water |  |  | 15 | 800kPa |  |  |  |  | George Fischer |  | Solvent cement socket | N/A |  |  |  |  | All PVC construction. Typ 360 complete with polypyrene s.g. = 0.09 (special) - so it floats
B | GT36-060-83.3 | VA83308 | Dosing Panel 2 | Ball Valve | Calibration Column Isolation Valve | Service Water |  |  | 15 | 800kPa |  |  |  |  | George Fischer |  | Solvent cement socket | N/A |  |  |  |  | All PVC construction
B | GT36-060-83.3 | VA83309 | Dosing Panel 2 | Ball Valve | FSA Supply from Tank 2 Isolation Valve | FSA |  |  | 15 | 800kPa |  |  |  |  | George Fischer |  | Solvent cement socket | N/A |  |  |  |  | All PVC construction
B | GT36-060-83.3 | VA83310 | Dosing Panel 2 | 3-way Valve | Service Water/ FSA Supply Water 3 way valve | FSA |  |  | 15 | 800kPa |  |  |  |  | George Fischer |  | Solvent cement socket | N/A |  |  |  |  | All PVC construction
B | GT36-060-83.3 | VA83312 | Dosing Panel 2 | Ball Valve | Pump Suction Isolation Valve | FSA |  |  | 15 | 800kPa |  |  |  |  | George Fischer |  | Solvent cement socket | N/A |  |  |  |  | All PVC construction
B | GT36-060-83.3 | VA83313 | Dosing Panel 2 | Pressure Relief Valve | Pump Relief Valve | FSA |  |  | 15 | 1000kPa |  |  |  |  | George Fischer |  | Solvent cement socket union | N/A |  |  |  |  | Pressure Setpoint: below lowest pressure rating of fittings/ equipment in downstream pipework, above pump max duty pressure but below pump IRV eg 600kPa. All PVC Construction
B | GT36-060-83.3 | VA83314 | Dosing Panel 2 | Ball Valve | Pump Discharge Isolation Valve | FSA |  |  | 15 | 800kPa |  |  |  |  | George Fischer |  | Solvent cement socket | N/A |  |  |  |  | All PVC construction
B | GT36-060-83.3 | VA83315 | Dosing Panel 2 | Ball Valve | Pulsation Dampener Isolation Valve | FSA |  |  | 15 | 800kPa |  |  |  |  | George Fischer |  | Solvent cement socket | N/A |  |  |  |  | All PVC construction
B | GT36-060-83.3 | VA83316 | Dosing Panel 2 | Ball Valve | Pressure Indicator Isolation Valve | FSA |  |  | 15 | 800kPa |  |  |  |  | George Fischer |  | Solvent cement socket | N/A |  |  |  |  | All PVC construction
B | GT36-060-83.3 | VA83317 | Dosing Panel 2 | Ball Valve | Magflow Inlet Isolation Valve | FSA |  |  | 15 | 800kPa |  |  |  |  | George Fischer |  | Solvent cement socket | N/A |  |  |  |  | All PVC construction
B | GT36-060-83.3 | VA83319 | Dosing Panel 2 | Pressure Sustaining Valve | Magflow PSV | FSA |  |  | 15 | 1000kPa |  |  |  |  | George Fischer |  | Solvent cement socket union | N/A |  |  |  |  | Pressure Setpoint: dose point back pressure + 200kPa eg 500kPa; All PVC Construction
B | GT36-060-83.3 | VA83320 | Dosing Panel 2 | Ball Valve | Magflow Outlet Isolation Valve | FSA |  |  | 15 | 800kPa |  |  |  |  | George Fischer |  | Solvent cement socket | N/A |  |  |  |  | All PVC construction
B | GT36-060-83.3 | VA83321 | Dosing Panel 2 | Ball Valve | Magflow Bypass Valve | FSA |  |  | 15 | 800kPa |  |  |  |  | George Fischer |  | Solvent cement socket | N/A |  |  |  |  | All PVC construction
B | GT36-060-83.3 | VA83322 | Dosing Panel 2 | Ball Valve | Air Vent Isolation Valve | FSA/ Air |  |  | 15 | 800kPa |  |  |  |  | George Fischer |  | Solvent cement socket | N/A |  |  |  |  | All PVC construction
B | GT36-060-83.3 | VA83323 | Dosing Panel 2 | Auto Air Vent Valve | Air Vent Valve | FSA/ Air |  |  | 15 | 800kPa |  |  |  |  | Stubbe or Equivalent |  | Solvent cement socket | N/A |  |  |  |  | All PVC construction Needs to be mounted vertically
B | GT36-060-83.3 | VA83324 | Dosing Panel 2 | Motorised 3-way Valve | FSA Supply/ Drip Tray Actuated 3-way Valve | FSA |  | 24V DC 2 SPDT Limit Switches | 15 | 800kPa |  |  |  |  | George Fischer |  | Solvent cement socket | N/A |  |  |  |  | All PVC construction Specifically T or L port
B | GT36-060-83.3 | VA83325 | Dosing Panel 2 | Ball Valve | FSA Supply/ Dose Point Isolation Valve | FSA |  |  | 15 | 800kPa |  |  |  |  | George Fischer |  | Solvent cement socket | N/A |  |  |  |  | All PVC construction
B | GT36-060-83.3 | VA83326 | Dosing Panel 2 | Non-return Valve | FSA Supply Non-return Valve | FSA |  |  | 15 | 800kPa |  |  |  |  | George Fischer |  | Solvent cement socket | N/A |  |  |  |  | All PVC construction
B | GT36-060-83.3 | VA83327 | Dosing Panel 2 | Ball Valve | Dilution Water Supply Isolation Valve | Chlorine Solution, Service Water or Sample Water |  |  | 25 | 800kPa |  |  |  |  | George Fischer |  | Solvent cement socket | N/A |  |  |  |  | All PVC construction
B | GT36-060-83.3 | VA83328 | Dosing Panel 2 | Non-return Valve | Dilution Water Supply Non-return Valve | Chlorine Solution, Service Water or Sample Water |  |  | 25 | 800kPa |  |  |  |  | George Fischer |  | Solvent cement socket | N/A |  |  |  |  | All PVC construction
B | GT36-060-83.3 | VA83329 | Dosing Panel 2 | Ball Valve | Dosing Panel 2 Isolation to Dose Point | Chlorine Solution, Service Water or Sample Water |  |  | 25 | 800kPa |  |  |  |  | George Fischer |  | Solvent cement socket | N/A |  |  |  |  | All PVC construction
VALVE SCHEDULE - FLUROSILICIC ACID: ANCILLARIES
ENGINEERING DESIGN | [14 empty] | ENGINEERING DESIGN DETAIL |  |  |  | PROCUREMENT
REVISION | P&ID DRAWING | TAG No. | FUNCTIONAL LOCATION | EQUIPMENT TYPE | EQUIPMENT DESCRIPTION | STATUS | POWER (kW) | VOLTAGE (V) | SIZE | DESIGN PRESSURE (KPA) | INPUT | OUTPUT | RANGE | SCALE | MAKE | MODEL | END CONNECTION TYPE | END CONNECTION STANDARD | SERIAL No. | SUPPLIER | INSTALLED BY | DATASHEET | COMMENTS
B | GT36-060-83.4 | VA83401 | Ancillaries | Valve | Dosing Panel Area Safety Shower Isolation Valve | Service Water |  |  | 25 | 800kPa |  |  |  |  | George Fischer |  | Solvent cement socket | N/A |  |  |  |  | Could also use braeco gate valve for this application
B | GT36-060-83.4 | VA83402 | Ancillaries | Valve | Load-in Panel Area Safety Shower Isolation Valve | Service Water |  |  | 25 | 800kPa |  |  |  |  | George Fischer |  | Solvent cement socket | N/A |  |  |  |  | Could also use braeco gate valve for this application
B | GT36-060-83.4 | VA83403 | Ancillaries | Valve | Load-in Apron Area Safety Shower Isolation Valve | Service Water |  |  | 25 | 800kPa |  |  |  |  | George Fischer |  | Solvent cement socket | N/A |  |  |  |  | Could also use braeco gate valve for this application
B | GT36-060-83.4 | VA83404 | Ancillaries | Valve | Dosing Panel Area Retractable Washdown Hose Isolation Valve | Service Water |  |  | 25 | 800kPa |  |  |  |  | George Fischer |  | Solvent cement socket | N/A |  |  |  |  | Could also use braeco gate valve for this application
B | GT36-060-83.4 | VA83405 | Ancillaries | Valve | Outdoor Load-in Panel Area Retractable Washdown Hose Isolation Valve | Service Water |  |  | 25 | 800kPa |  |  |  |  | George Fischer |  | Solvent cement socket | N/A |  |  |  |  | Could also use braeco gate valve for this application
B | GT36-060-83.4 | VA83406 | Ancillaries | Diaphragm Valve | Manual Treated Sampling Point Valve | Sample Potable Water |  |  | 15 | 1000kPa |  |  |  |  | George Fischer |  | Solvent cement socket | N/A |  |  |  |  | Pressure requirements determined by analyser selected and site system pressures.
B | GT36-060-83.4 | VA83407 | Ancillaries | Pressure Reducing Valve | Sample Flow PRV | Sample Potable Water |  |  | 15 | 1000kPa |  |  |  |  | George Fischer |  | Solvent cement socket | N/A |  |  |  |  | Pressure requirements determined by analyser selected and site system pressures.
B | GT36-060-83.4 | VA83408 | Ancillaries | Ball Valve | Inlet Main Isolation Valve | Sample Potable Water |  |  | 15 | 1000kPa |  |  |  |  | George Fischer |  | Solvent cement socket | N/A |  |  |  |  | May be included with panel mounted analysers
B | GT36-060-83.4 | VA83409 | Ancillaries | Needle Valve | Sample Needle Valve | Sample Potable Water |  |  | 15 | 1000kPa |  |  |  |  | George Fischer |  | Solvent cement socket | N/A |  |  |  |  | May be included with panel mounted analysers
B | GT36-060-83.4 | VA83410 | Ancillaries | Diaphragm Valve | Site Service Diaphragm Valve | Service Water |  |  | 25 | 800kPa |  |  |  |  | George Fischer |  | Solvent cement socket | N/A
B | GT36-060-83.4 | VA83412 | Ancillaries | Ball Valve | Sample Water Return Isolation Valve | Service Water |  |  | 25 | 800kPa |  |  |  |  | George Fischer |  | Solvent cement socket | N/A
B | GT36-060-83.4 | VA83413 | Ancillaries | Ball Valve | Sample Pump Suction Valve | Service Water |  |  | 25 | 800kPa |  |  |  |  | George Fischer |  | Solvent cement socket | N/A |  |  |  |  | Required only if sample water return is utilised as dilution water
B | GT36-060-83.4 | VA83414 | Ancillaries | Non-return Valve | Sample Pump Non-return Valve | Sample Potable Water |  |  | 15 | [5 empty] | George Fischer |  | Solvent cement socket | N/A
B | GT36-060-83.4 | VA83415 | Ancillaries | Diaphragm Valve | Sample Pump Diaphragm Valve | Sample Potable Water |  |  | 15 | [5 empty] | George Fischer |  | Solvent cement socket | N/A
B | GT36-060-83.4 | VA83416 | Ancillaries | Ball Valve | Sample Pump Discharge Valve | Sample Potable Water |  |  | 15 | [5 empty] | George Fischer |  | Solvent cement socket | N/A

## Pump
DESIGN | [20 empty] | CONSTRUCTION / COMISSIONING
Asset ID | Description - Asset | Type of Pump | Manufacture / Make | Model Number / ID | Weight | Material - Pump Casing | Material - Lining | Diameter - Impeller Max. | Type of Impeller | Type of Seal | Pump Design Max. Flowrate (L/s) | Pump Design Min. Flowrate (L/s) | Pump Design Head at Max. Flow (MHW) | Pump Design Head at Min Flow (MHW) | Speed at Max. Flowrate | Type of Connection | Type of Bearings | Type of Wear Ring | Mounting Configuration | Expected Asset Life (yrs) | Serial Number | Acquisitions Cost | Date - Manufactured | Date - Acquired | Date - Warranty Expire | As-Constructed Reference

## Motor
DESIGN | [12 empty] | CONSTRUCTION / COMISSIONING
Asset ID | Description - Asset | Type of Motor | Manufacture / Make | Model Number / ID | Power | Rated Voltage | Rated Current | Weight | Ex Rating | Ingress Protection (IP) Rating | Insulation Class | Expected Asset Life (yrs) | Serial Number | Acquisitions Cost | Date - Manufactured | Date - Acquired | Date - Warranty Expire | As-Constructed Reference