## FuncDescriptOverview
FSA STANDARD DESIGN - TWO TANKS & TWO PANELS SYSTEM
FUNCTIONAL DESCRIPTION OVERVIEW Rev 2.1 26.05.23
Note: Any digital ouput (DO) for the FLIP is shown in the PLC column as "Modbus". This is done only for convienience.
Object No. | Asset / Process | P&ID Tag | Physical Description | I/O Type |  |  | State 0 | State 1 | Control / Interlock / Permissive |  | Location / Setting (C=Control, D=Display) |  |  | Severity | Data Hist
|  |  |  | Local | PLC | SM |  |  | ( >> triggers, << triggered by ) |  | Local | OIP (FLIP) | HMI |  | (Yes/No)
83110 | FSA Tank 1 | LI83110 | Magnetic Level Indicator | Local
|  | LSHH83110 | High High Sensing Level Switch |  | DI |  | Alarm | Normal | >> | Alerts tank is close to overflowing. Includes Audible alarm on Load-in Panel and cuts power to load-in area power outlet (where provided) | D*
|  | LAHH83110 | High High Level Alarm |  |  | DI | Normal | Alarm | >> | Alerts tank is close to overflowing. |  | D | D | Critical | Yes
* Direct "hard-wired" connection
83111 | FSA System 1 | HS83111 | Master Mode Select Hand Switch |  |  | DI |  |  | >> | Allows Operator selection of FSA System 1 control mode (Dosing, Flushing, Calibration, Manual, Stopped) |  | C | C note 1
83113 | FSA Tank 1 | LT83113 | Level (Pressure) Transmitter
|  | LI83113 | Level Indicator |  | AI | [5 empty] | D*
[6 empty] | AI | [5 empty] | D | D |  | Yes
|  | LAH83113 | High Level Alarm |  |  | DI | Normal | Alarm | >> | Notifies delivery tanker operator to stop filling. | D* | D | D | Urgent | Yes
|  | LAL83113 | Low Level Alarm |  |  | DI | Normal | Alarm | >> | Alerts operator to order more chemical. |  | D | D | Warning | Yes
|  | LALL83113 | Low Low Level Alarm |  |  | DI | Normal | Alarm | >> | Interlock - Inhibit or shutdown Dosing Mode (dosing pump dry run protection) |  | D | D | Critical | Yes
|  | HS83113 | Alarm Acknowledge Hand Switch |  | DI |  | Off | On | >> | Acknowledge Audible alarm | C
* Direct "hard-wired" connection
83117 | FSA Tank 1 Isolation Valve | ZZH83117 | Open Valve |  | DO |  | Off | Open | << | Permissive - Dosing Mode Selected on HS83111
| (Type 2 Valve) | ZZL83117 | Close Valve |  | DO |  | Off | Close | << | Interlock - Flushing Mode Selected+K151
[9 empty] | << | Interlock - Calibration Mode Selected on HS83111
[9 empty] | << | Interlock - Stopped Mode Selected on HS83111
[9 empty] | << | Interlock - Bund Sump Conductivity High Alarm (AAH83136) AND Bund Sump level High Alarm (LAH83135) activated
|  | ZSH83117 | Valve Open Limit Switch |  | DI |  | Off | Open
|  | ZSL83117 | Valve Close Limit Switch |  | DI |  | Off | Close
|  | ZIH83117 | Valve Open Indicator |  |  | DI | Off | Open |  |  |  | D | D |  | Yes
|  | ZIL83117 | Valve Close Indicator |  |  | DI | Off | Close |  |  |  | D | D |  | No
|  | ZA83117 | Valve Fault |  |  | DI | Normal | Alarm | >> | Interlock - Inhibits or shutdown Operating Mode |  | D | D | Warning | Yes
|  | HS83117 | Switch on FLIP to Open/Close FSA Storage Tank 1 isolation valve |  | Modbus |  | Closed | Open | >> | Switch tracks & holds last valve position when entering manual mode on HS83111. |  | C
83118 | FSA Tank 1 Acid/Water Selector Valve | ZZH83118 | Open Valve to Acid |  | DO |  | Off | Open | << | Interlock - Dosing Mode Selected on HS83111
| (Type 2 Valve) | [7 empty] | >> | Interlock - force/hold Dose/Drain Valve (VA83224) to Dose position IF Manual Mode Selected on HS83111
|  | ZZL83118 | Close Valve to Acid (Open Valve to Water) |  | DO |  | Off | Close | << | Interlock - Flushing Mode Selected on HS83111
[9 empty] | << | Interlock - Calibration Mode Selected on HS83111
|  | ZSH83118 | Valve to Acid Open Limit Switch |  | DI |  | Off | Open
|  | ZSL83118 | Valve to Acid Close (Valve to Water Open) Limit Switch |  | DI |  | Off | Close
|  | ZIH83118 | Valve to Acid Open Indicator |  |  | DI | Off | Open |  |  |  | D | D |  | Yes
|  | ZIL83118 | Valve to Acid Close (Valve to Water Open) Indicator |  |  | DI | Off | Close |  |  |  | D | D |  | No
|  | ZA83118 | Valve Fault |  |  | DI | Normal | Alarm | >> | Interlock - Inhibits or shutdown Operating Mode |  | D | D | Warning | Yes
|  | HS83118 | Switch on FLIP to select Tank 1 acid/water selector valve position |  | Modbus |  | Off | On | >> | Switch tracks & holds last valve position when entering manual mode on HS83111 |  | C
83120 | FSA Tank 2 | LI83120 | Magnetic Level Indicator | Local
|  | LSHH83120 | High High Sensing Level Switch |  | DI |  | Alarm | Normal |  |  | D*
|  | LAHH83120 | High High Level Alarm |  |  | DI | Normal | Alarm | >> | Alerts tank is close to overflowing. Includes Audible alarm on Load-in Panel and cuts power to load-in area power outlet |  | D | D | Critical | Yes
* Direct "hard-wired" connection
83121 | FSA System 2 | HS83121 | Master Mode Select Hand Switch |  |  | DI |  |  | >> | Allows Operator selection of FSA System 2 control mode (Dosing, Flushing, Calibration, Manual, Stopped) |  | C | C note 1
83123 | FSA Tank 2 | LT83123 | Level (Pressure) Transmitter
|  | LI83123 | Level Indicator |  | AI | [5 empty] | D*
[6 empty] | AI | [5 empty] | D | D |  | Yes
|  | LAH83123 | High Level Alarm |  |  | DI | Normal | Alarm | >> | Notifies delivery tanker operator to stop filling. | D* | D | D | Urgent | Yes
|  | LAL83123 | Low Level Alarm |  |  | DI | Normal | Alarm | >> | Alerts operator to order more chemical. |  | D | D | Warning | Yes
|  | LALL83123 | Low Low Level Alarm |  |  | DI | Normal | Alarm | >> | Interlock - Inhibit or shutdown Dosing Mode (dosing pump dry run protection) |  | D | D | Critical | Yes
|  | HS83123 | Alarm Acknowledge Hand Switch |  | DI |  | Off | On |  | Acknowledge Audible alarm | C
* Direct "hard-wired" connection
83127 | FSA Tank 2 Isolation Valve | ZZH83127 | Open Valve |  | DO |  | Off | Open | << | Permissive - Dosing Mode Selected on HS83121
| (Type 2 Valve) | ZZL83127 | Close Valve |  | DO |  | Off | Close | << | Interlock - Flushing Mode Selected on HS83121
[9 empty] | << | Interlock - Calibration Mode Selected on HS83121
[9 empty] | << | Interlock - Stopped Mode Selected on HS83121
[9 empty] | << | Interlock - Bund Sump Conductivity High Alarm (AAH83136) AND Bund Sump level High Alarm (LAH83135) activated
|  | ZSH83127 | Valve Open Limit Switch |  | DI |  | Off | Open
|  | ZSL83127 | Valve Close Limit Switch |  | DI |  | Off | Close
|  | ZIH83127 | Valve Open Indicator |  |  | DI | Off | Open |  |  |  | D | D |  | Yes
|  | ZIL83127 | Valve Close Indicator |  |  | DI | Off | Close |  |  |  | D | D |  | No
|  | ZA83127 | Valve Fault |  |  | DI | Normal | Alarm | >> | Interlock - Inhibits or shutdown Operating Mode |  | D | D | Warning | Yes
|  | HS83127 | Switch on FLIP to Open/Close FSA Storage Tank 2 isolation valve |  | Modbus |  | Closed | Open | >> | Switch tracks & holds last valve position when entering manual mode on HS83121 |  | C
83128 | FSA Tank 2 Acid/Water Selector Valve | ZZH83128 | Open Valve to Acid |  | DO |  | Off | Open | << | Interlock - Dosing Mode Selected on HS83121
| (Type 2 Valve) | [7 empty] | >> | Interlock - force and hold Dose/Drain Valve (VA83324) to Dose position IF Manual Mode Selected
|  | ZZL83128 | Close Valve to Acid (Open Valve to Water) |  | DO |  | Off | Close | << | Interlock - Flushing Mode Selected on HS83121
[9 empty] | << | Interlock - Calibration Mode Selected on HS83121
|  | ZSH83128 | Valve to Acid Open Limit Switch |  | DI |  | Off | Open
|  | ZSL83128 | Valve to Acid Close (Valve to Water Open) Limit Switch |  | DI |  | Off | Close
|  | ZIH83128 | Valve to Acid Open Indicator |  |  | DI | Off | Open |  |  |  | D | D |  | Yes
|  | ZIL83128 | Valve to Acid Close (Valve to Water Open) Indicator |  |  | DI | Off | Close |  |  |  | D | D |  | No
|  | ZA83128 | Valve Fault |  |  | DI | Normal | Alarm | >> | Interlock - Inhibits or shutdown Operating Mode |  | D | D | Warning | Yes
|  | HS83128 | Switch on FLIP to select Tank 2 acid/water selector valve position |  | Modbus |  | Off | On | >> | Switch tracks & holds last valve position when entering manual mode on HS83121 |  | C
83132 | FSA Tank 1 Service Water Flushing Valve | ZZH83132 | Open Valve |  | DO |  | Off | Open | << | Interlock - Flushing Mode Selected on HS83111
| (Type 2 Valve) | ZZL83132 | Close Valve |  | DO |  | Off | Close | << | Interlock - Dosing Mode Selected on HS83111
[9 empty] | << | Interlock - Calibration Mode Selected on HS83111
[9 empty] | << | Interlock - Stopped Mode Selected on HS83111
|  | ZSH83132 | Valve Open Limit Switch |  | DI |  | Off | Open
|  | ZSL83132 | Valve Close Limit Switch |  | DI |  | Off | Close
|  | ZIH83132 | Valve Open Indicator |  |  | DI | Off | Open |  |  |  | D | D |  | Yes
|  | ZIL83132 | Valve Close Indicator |  |  | DI | Off | Close |  |  |  | D | D |  | No
|  | ZA83132 | Valve Fault |  |  | DI | Normal | Alarm | >> | Interlock - Inhibits or shutdown Operating Mode |  | D | D | Warning | Yes
|  | HS83132 | Switch on FLIP to open/close Tank 1 Flushing Water Valve |  | Modbus |  | Closed | Open | >> | Switch tracks & holds last valve position when entering manual mode on HS83111 |  | C
83134 | FSA Tank 2 Service Water Flushing Valve | ZZH83134 | Open Valve |  | DO |  | Off | Open | << | Interlock - Flushing Mode Selected on HS83121
| (Type 2 Valve) | ZZL83134 | Close Valve |  | DO |  | Off | Close | << | Interlock - Dosing Mode Selected on HS83121
[9 empty] | << | Interlock - Calibration Mode Selected on HS83121
[9 empty] | << | Interlock - Stopped Mode Selected on HS83121
|  | ZSH83134 | Valve Open Limit Switch |  | DI |  | Off | Open
|  | ZSL83134 | Valve Close Limit Switch |  | DI |  | Off | Close
|  | ZIH83134 | Valve Open Indicator |  |  | DI | Off | Open |  |  |  | D | D |  | Yes
|  | ZIL83134 | Valve Close Indicator |  |  | DI | Off | Close |  |  |  | D | D |  | No
|  | ZA83134 | Valve Fault |  |  | DI | Normal | Alarm | >> | Interlock - Inhibits or shutdown Operating Mode |  | D | D | Warning | Yes
|  | HS83134 | Switch on FLIP to open/close Tank 2 Flushing Water Valve |  | Modbus |  | Closed | Open | >> | Switch tracks & holds last valve position when entering manual mode on HS83121 |  | C
83135 | Bund Sump | LSH83135 | High Sensing Level Switch |  | DI |  | Alarm | Normal
|  | LAH83135 | High Level Alarm |  |  | DI | Normal | Alarm | >> | Interlock - closes FSA Tank Isolation Valves IF Bund Sump Conductivity High Alarm activated |  | D | D | Urgent | Yes
83136 | Bund Sump | AIT83136 | Conductivity Transmitter | Local | [6 empty] | D*
|  | AI83136 | Conductivity Indicator |  | AI
[6 empty] | AI | [5 empty] | D | D |  | Yes
|  | AAH83136 | High Conductivity Alarm |  |  | DI | Normal | Alarm | >> | Interlock - closes Bund Sump Drain Valve (or prevents opening) |  | D | D | Urgent | Yes
[9 empty] | >> | Interlock - closes FSA Tank Isolation Valves IF Bund Sump Level High Alarm activated |  | D | D | Urgent | Yes
|  | AAHH83136 | High High Conductivity Alarm |  |  | DI | Normal | Alarm |  |  |  | D | D | Critical | Yes
* Direct "hard-wired" connection
83137 | Bund Sump Drain Valve | ZZH83137 | Open Valve |  | DO |  | Off | Open
|  | ZZL83137 | Close Valve |  | DO |  | Off | Close | << | Interlock - Bund Sump Conductivity High Alarm activated
[9 empty] | << | Interlock - Valve is timed to open only 5 minutes
|  | ZSH83137 | Valve Open Limit Switch |  | DI |  | Off | Open
|  | ZSL83137 | Valve Close Limit Switch |  | DI |  | Off | Close
|  | ZIH83137 | Valve Open Indicator |  |  | DI | Off | Open |  |  |  | D | D |  | Yes
|  | ZIL83137 | Valve Close Indicator |  |  | DI | Off | Close |  |  |  | D | D |  | Yes
|  | ZA83137 | Valve Fault |  |  | DI | Normal | Alarm |  |  |  | D | D | Warning | Yes
|  | HS83137B | Override Key |  | DI |  | Off | On | >> | Permissive - Overrides valve VA83137 High Conductivity interlock |  | C
|  | HS83137A | Switch to open/close valve manually at FLIP |  | Modbus |  | Closed | Open |  |  |  | C
83138 | Load-in apron sump Drainage/Waste Holding Tank Selector Valve | LSH83138 | Load in apron sump - High Level switch |  | DI |  | Normal | Alarm
|  | LAH83138 | Load in apron sump - High Level Alarm |  |  | DI | Normal | Alarm |  |  |  | D | D | Warning
|  | ZZH83138 | Open Valve to Drainage |  | DO |  | Off | Open | << | YS83106 Load-in door switch off (door closed) if HS83138A is in Auto
[9 empty] | << | HS83138B in Off position (Open to Drainage selected) if HS83138A is in Manual
|  | ZZL83138 | Open Valve to Waste Holding Tank |  | DO |  | Off | Close | << | YS83106 Load-in door switch On (door open) if HS83138A is in Auto
[9 empty] | << | HS83138B On (Open to Waste selected) if HS83138A is in Manual
|  | ZSH83138 | Valve to Drainage Open Limit Switch |  | DI |  | Off | Open | >> | ZIH83138
|  | ZSL83138 | Valve to Waste Holding Tank Open Limit Switch |  | DI |  | Off | Close | >> | ZIL83138
|  | HS83138A | Override selector automatic/manual Hand Switch |  | Modbus | DO | Auto | Manual | >> | When in Automatic mode: Valve VA83138 control is by load-in door switch YS83106 interlock and HS83138A is ignored. |  | C | C |  | Yes
[9 empty] | >> | When in manual mode: Valve VA83138 control is by HS83138B and load-in door switch YS83106 interlock is ignored
|  | HS83138B | Drainage/Waste Holding Tank Selector Hand Switch |  | Modbus | DO | Off | On | >> | Functionality to select 3-way valve opening to Drainage/Waste Holding Tank when HS83138A is in manual mode |  | C | C
|  | ZIH83138 | Valve to Drainage Open Indicator |  |  | DI | Off | Open | << | ZSH83138 |  | D | D |  | Yes
|  | ZIL83138 | Valve to Waste Holding Tank Open Indicator |  |  | DI | Off | Close | << | ZSL83138 |  | D | D
|  | ZA 83138 | Valve Fault |  |  | DI | Normal | Alarm |  | Notifies valve VA83138 failing to reach required position (ie ZIL83138, ZIH83138) |  | D | D | Warning | Yes
83106 | Load in door | YS83106 | Load-in door switch |  | DI |  | Off | On | << | Activated by the opening of the load in door (door in front of load in panel) | C
[9 empty] | >> | Activates YI83106 on HMI and FLIP screens "Load-in Door Open"
[9 empty] | >> | When activated (ie. load in door is open), opens 3-way valve VA83138 to wasteholding tank (drain is closed)
[9 empty] | << | Deactivated by the closing of the load in door
[9 empty] | >> | When deactivated (ie. load in door is closed), opens 3-way valve VA83138 to drain (waste holding tank is closed)
|  | YI83106 | Load in Door open indicator |  |  | DI | Off | Open | << | Activated when YS83106 is activated |  | D | D |  | Yes
83144 | Waste Holding Tank | LSH83144 | High Level Switch |  | DI |  | Alarm | Normal
|  | LAH83144 | High Level Alarm |  |  | DI | Normal | Alarm | >> | Alerts Operator to order Disposal tanker |  | D | D | Warning | Yes
83202 | FSA Panel 1 Dilution Water Valve | ZZH83202 | Open Valve |  | DO |  | Off | Open | << | Interlock - Dosing Mode Selected on HS83111
| (Type 2 Valve) | [7 empty] | << | Interlock - Flushing Mode Selected on HS83111
[9 empty] | << | Interlock - Calibration Mode Selected on HS83111
|  | ZZL83202 | Close Valve |  | DO |  | Off | Close | << | Interlock - Stopped Mode selected on HS83111. If chlorine solution is used as dilution water, at least one Dilution water valve (Panel 1 or 2) must be open at all times.
|  | ZSH83202 | Valve Open Limit Switch |  | DI |  | Off | Open
|  | ZSL83202 | Valve Close Limit Switch |  | DI |  | Off | Close
|  | ZIH83202 | Valve Open Indicator |  |  | DI | Off | Open |  |  |  | D | D |  | Yes
|  | ZIL83202 | Valve Close Indicator |  |  | DI | Off | Close |  |  |  | D | D |  | No
|  | ZA83202 | Valve Fault |  |  | DI | Normal | Alarm | >> | Interlock - Inhibits or shutdown Operating Mode on HS83111. If chlorine solution is used as dilution water, at least one Dilution water valve (Panel 1 or 2) must be open at all times. |  | D | D | Warning | Yes
83205 | FSA Panel 1 Dilution Water Flow | FSL83205 | Dilution Low Flow Switch |  | DI |  | Alarm | Normal |  | If chlorine solution is used as dilution water, chlorine system Low Flow Switch FSL81XXX will perform this duty.
|  | FAL83205 | Dilution Low Flow Alarm |  |  | DI | Normal | Alarm | >> | Interlock - Inhibits or shutdown Operating Mode & changeover to standby system |  | D | D | Warning | Yes
83213 | FSA Panel 1 Pump | IY83213 | Run Pump |  | DO |  | Stopped | Running | << | Interlock (Auto Control) - Dosing Mode Selected on HS83111 AND FITXXXXX > setpoint Xm3/h
[9 empty] | << | Interlock (Auto Control) - Flushing Mode Selected on HS83111
[9 empty] | << | Permissive (Manual Control) - Calibration or Manual Mode Selected on HS83111
|  | YS83213B | Pump Running Switch |  | DI |  | Stopped | Running
|  | YL83213 | Pump Running Indicator |  |  | DI | Stopped | Running |  |  |  | D | D |  | Yes
|  | HS83213 | Pump Control Auto / Manual Hand Switch |  |  | DO |  |  | >> | Selects auto or manual pump control |  | C |  |  | Yes
|  | HC83213A | Pump Speed Manual Adjustment |  |  | AO |  |  | >> | Manual adjustment of Pump Speed if on HS83111 in Calibration or Manual Modes |  | C |  |  | Yes
|  | HC83213B | Pump Stroke Manual Adjustment | Local |  |  |  |  | >> | Manual adjustment of Pump Stroke Length (for pump with purely physical manual stroke adjustment, not via FLIP or HMI) | C
|  | HC83213C | Min. Pump Speed Setpoint |  |  | AO |  |  | >> | Data used to prevent Pump running underspeed |  | C | C |  | Yes
|  | SY83213 | Pump Speed Calculation / Adjustment |  | AO |  |  |  | >> | Set Pump Speed in all Modes
|  | SI83213 | Pump Speed Indicator |  | AI
[6 empty] | AI | [5 empty] | D | D |  | Yes
|  | YS83213A | Pump Diaphragm Leak Switch |  | DI |  | Fault | Normal
|  | YA83213A | Pump Diaphragm Leak Alarm |  |  | DI | Normal | Alarm | >> | Interlock - Initiates shutdown of Dosing system and changeover to standby system |  | D | D | Urgent | Yes
|  | YS83213C | Pump Motor Protection Fault Switch |  | DI |  | Normal | Fault
|  | YA83213B | Pump Motor Protection Fault Alarm |  |  | DI | Normal | Alarm | >> | Interlock - Initiates shutdown of Dosing system and changeover to standby system |  | D | D | Urgent | Yes
|  | KQT83213 | Pump Hours Run |  |  | AI | [5 empty] | D | D |  | Yes
83218 | FSA Panel 1 Pump Flow | FIT83218 | Flow Transmitter | Local | [6 empty] | D*
|  | FI83218 | Flow Indicator |  | AI
[6 empty] | AI |  |  | >> | Signal used for PID trim of Dosing pump PU83213 |  | D | D |  | Yes
|  | FQT83218 | Totalised Flow Pulse Transmitter |  | DI
|  | FQI83218A | Totalised Flow (Calc) |  |  | AI | [5 empty] | D | D |  | Yes
|  | FQI83218B | Daily Consumption Flow (Calc) |  |  | AI | [6 empty] | D |  | Yes
|  | YA83218 | Flow Deviation Alarm |  |  | DI | Normal | Alarm | << | Initiates IF Pump flow deviates +/- from setpoint flow by > 10% |  |  | D | Critical | Yes
* Direct "hard-wired" connection
83231 | FSA 1 Calculated Actual Fluoride Dose Rate | HC83231A | Raw Water Background Fluoride Level |  |  | AO |  |  | >> | Data used in PLC to calculate FSA Flow Rate Required and Set Speed of Pump |  | C | C |  | Yes
|  | HC83231B | Delivered Acid Concentration (%) |  |  | AO |  |  | >> | Data used in PLC to calculate FSA Flow Rate Required and Set Speed of Pump |  | C | C |  | Yes
|  | HC83231C | TW Target Fluoride Dose Rate Set Point |  |  | AO |  |  | >> | Data used in PLC to calculate FSA Flow Rate Required and Set Speed of Pump |  | C | C |  | Yes
|  | HS83231 | Dose Rate Auto / Manual Hand Switch |  |  | DO |  |  | >> | Selects Auto trim or Manually entered dose rate. |  | C | C |  | Yes
|  | HC83231D | Manual Fluoride Dose Rate Set Point |  |  | AO |  |  | >> | Data used if HS83111 in Manual Mode to calculate FSA Flow Rate Required and Set Speed of Pump |  | C | C |  | Yes
|  | FI83231A | Calculated Actual Fluoride Dose Rate Indicator |  |  | AI | [5 empty] | D | D |  | Yes
|  | FI83231B | PID Controller Dose Rate Set Point Indicator |  |  | AI | [6 empty] | D |  | Yes
|  | FAH83231 | Dose Rate High Alarm |  |  | DI | Normal | Alarm |  |  |  | D | D | Urgent | Yes
|  | FAHH83231 | Dose Rate High High Alarm |  |  | DI | Normal | Alarm | >> | Initiates shutdown of Dosing system and changeover to standby system |  | D | D | Critical | Yes
|  | FAL83231 | Dose Rate Low Alarm |  |  | DI | Normal | Alarm |  |  |  | D | D | Urgent | Yes
|  | FALL83231 | Dose Rate Low Low Alarm |  |  | DI | Normal | Alarm | >> | Initiates shutdown of Dosing system and changeover to standby system |  | D | D | Critical | Yes
XXXXX | Clearwater Flow | FITXXXXX | Clearwater Flow Rate |  | AI |  |  |  | >> | Data used in PLC to calculate FSA Flow Rate Required and Set Speed of Pump. Flow must exceed setpoint Xm3/h before control loop activation. |  |  |  |  | Yes
83224 | FSA Panel 1 Dose/Drain Valve | ZZH83224 | Open Valve to Dose |  | DO |  | Off | Open | << | Interlock - Dosing Mode Selected on HS83111
| (Type 2 Valve) | [7 empty] | << | Interlock (initially) - Flushing Mode Selected on HS83111
[9 empty] | << | Interlock - Calibration Mode Selected on HS83111
[9 empty] | << | Interlock - If Manual Mode Selected on HS83111 AND Acid/Water Valve (VA83118) opened to acid then set to Dose position (open)
|  | ZZL83224 | Close Valve to Dose (Open Valve to Drain) |  | DO |  | Off | Close | << | Permissive (after initial opening) - Flushing Mode Selected on HS83111
|  | ZSH83224 | Valve to Dose Open Limit Switch |  | DI |  | Off | Open
|  | ZSL83224 | Valve to Dose Close (Valve to Drain Open) Limit Switch |  | DI |  | Off | Close
|  | ZIH83224 | Valve to Dose Open Indicator |  |  | DI | Off | Open |  |  |  | D | D |  | Yes
|  | ZIL83224 | Valve to Dose Close (Valve to Drain Open) Indicator |  |  | DI | Off | Close |  |  |  | D | D |  | No
|  | ZA83224 | Valve Fault |  |  | DI | Normal | Alarm | >> | Interlock - Inhibits or shutdown Operating Mode on HS83111 |  | D | D | Warning | Yes
83302 | FSA Panel 2 Dilution Water Valve | ZZH83302 | Open Valve |  | DO |  | Off | Open | << | Interlock - Dosing Mode Selected on HS83121
| (Type 2 Valve) | [7 empty] | << | Interlock - Flushing Mode Selected on HS83121
[9 empty] | << | Interlock - Calibration Mode Selected on HS83121
|  | ZZL83302 | Close Valve |  | DO |  | Off | Close | << | Interlock - Stopped Mode selected on HS83121. If chlorine solution is used as dilution water, at least one Dilution water valve (Panel 1 or 2) must be open at all times.
|  | ZSH83302 | Valve Open Limit Switch |  | DI |  | Off | Open
|  | ZSL83302 | Valve Close Limit Switch |  | DI |  | Off | Close
|  | ZIH83302 | Valve Open Indicator |  |  | DI | Off | Open |  |  |  | D | D |  | Yes
|  | ZIL83302 | Valve Close Indicator |  |  | DI | Off | Close |  |  |  | D | D |  | No
|  | ZA83302 | Valve Fault |  |  | DI | Normal | Alarm | >> | Interlock - Inhibits or shutdown Operating Mode. If chlorine solution is used as dilution water, at least one Dilution water valve (Panel 1 or 2) must be open at all times. |  | D | D | Warning | Yes
83305 | FSA Panel 2 Dilution Water Flow | FSL83305 | Dilution Low Flow Switch |  | DI |  | Alarm | Normal |  | If chlorine solution is used as dilution water, chlorine system Low Flow Switch FSL81XXX will perform this duty.
|  | FAL83305 | Dilution Low Flow Alarm |  |  | DI | Normal | Alarm | >> | Interlock - Inhibits or shutdown Operating Mode |  | D | D | Warning | Yes
83313 | FSA Panel 2 Pump | IY83313 | Run Pump |  | DO |  | Stopped | Running | << | Interlock (Auto Control) - Dosing Mode Selected on HS83121 AND FITXXXXX > setpoint Xm3/h
[9 empty] | << | Interlock (Auto Control) - Flushing Mode Selected on HS83121
[9 empty] | << | Permissive (Manual Control) - Calibration Mode Selected on HS83121
|  | YS83313B | Pump Running Switch |  | DI |  | Stopped | Running
|  | YL83313 | Pump Running Indicator |  |  | DI | Stopped | Running |  |  |  | D | D |  | Yes
|  | HS83313 | Pump Control Auto / Manual Hand Switch |  |  | DO |  |  | >> | Selects auto or manual pump control |  | C |  |  | Yes
|  | HC83313A | Pump Speed Manual Adjustment |  |  | AO |  |  | >> | Manual adjustment of Pump Speed if HS83121 in Calibration or Manual Mode |  | C |  |  | Yes
|  | HC83313B | Pump Stroke Manual Adjustment | Local |  |  |  |  | >> | Manual adjustment of Pump Stroke Length (for pump with purely physical manual stroke adjustment, not via FLIP or HMI) | C
|  | HC83313C | Min. Pump Speed Setpoint |  |  | AO |  |  | >> | Data used to prevent Pump running underspeed |  | C | C |  | Yes
|  | SY83313 | Pump Speed Calculation / Adjustment |  | AO |  |  |  | >> | Set Pump Speed in all Modes
|  | SI83313 | Pump Speed Indicator |  | AI
[6 empty] | AI | [5 empty] | D | D |  | Yes
|  | YS83313A | Pump Diaphragm Leak Switch |  | DI |  | Fault | Normal
|  | YA83313A | Pump Diaphragm Leak Alarm |  |  | DI | Normal | Alarm | >> | Interlock - Initiates shutdown of Dosing system and changeover to standby system |  | D | D | Urgent | Yes
|  | YS83313C | Pump Motor Protection Fault Switch |  | DI |  | Normal | Fault
|  | YA83313B | Pump Motor Protection Fault Alarm |  |  | DI | Normal | Alarm | >> | Interlock - Initiates shutdown of Dosing system and changeover to standby system |  | D | D | Urgent | Yes
|  | KQT83313 | Pump Hours Run |  |  | AI | [5 empty] | D | D |  | Yes
83318 | FSA Panel 2 Pump Flow | FIT83318 | Flow Transmitter | Local | [6 empty] | D*
|  | FI83318 | Flow Indicator |  | AI
[6 empty] | AI |  |  | >> | Signal used for PID trim of Dosing pump PU83313 |  | D | D |  | Yes
|  | FQT83318 | Totalised Flow Pulse Transmitter |  | DI
|  | FQI83318A | Totalised Flow (Calc) |  |  | AI | [5 empty] | D | D |  | Yes
|  | FQI83318B | Daily Consumption Flow (Calc) |  |  | AI | [6 empty] | D |  | Yes
|  | YA83318 | Flow Deviation Alarm |  |  | DI | Normal | Alarm | << | Initiates IF Pump flow deviates +/- from setpoint flow by > 10% |  |  | D | Critical | Yes
* Direct "hard-wired" connection
83331 | FSA 2 Calculated Actual Fluoride Dose Rate | HC83331A | Raw Water Background Fluoride Level |  |  | AO |  |  | >> | Data used in PLC to calculate FSA Flow Rate Required and Set Speed of Pump |  | C | C |  | Yes
|  | HC83331B | Delivered Acid Concentration (%) |  |  | AO |  |  | >> | Data used in PLC to calculate FSA Flow Rate Required and Set Speed of Pump |  | C | C |  | Yes
|  | HC83331C | TW Target Fluoride Dose Rate Set Point |  |  | AO |  |  | >> | Data used in PLC to calculate FSA Flow Rate Required and Set Speed of Pump |  | C | C |  | Yes
|  | HS83331 | Dose Rate Auto / Manual Hand Switch |  |  | DO |  |  | >> | Selects Auto trim or Manually entered dose rate. |  | C | C |  | Yes
|  | HC83331D | Manual Fluoride Dose Rate Set Point |  |  | AO |  |  | >> | Data used if HS83121 in Manual Mode to calculate FSA Flow Rate Required and Set Speed of Pump |  | C | C |  | Yes
|  | FI83331A | Calculated Actual Fluoride Dose Rate Indicator |  |  | AI | [5 empty] | D | D |  | Yes
|  | FI83331B | PID Controller Dose Rate Set Point Indicator |  |  | AI | [6 empty] | D |  | Yes
|  | FAH83331 | Dose Rate High Alarm |  |  | DI | Normal | Alarm |  |  |  | D | D | Urgent | Yes
|  | FAHH83331 | Dose Rate High High Alarm |  |  | DI | Normal | Alarm | >> | Initiates shutdown of Dosing system and changeover to standby system |  | D | D | Critical | Yes
|  | FAL83331 | Dose Rate Low Alarm |  |  | DI | Normal | Alarm |  |  |  | D | D | Urgent | Yes
|  | FALL83331 | Dose Rate Low Low Alarm |  |  | DI | Normal | Alarm | >> | Initiates shutdown of Dosing system and changeover to standby system |  | D | D | Critical | Yes
83324 | FSA Panel 2 Dose/Drain Valve | ZZH83324 | Open Valve to Dose |  | DO |  | Off | Open | << | Interlock - Dosing Mode Selected on HS83121
| (Type 2 Valve) | [7 empty] | << | Interlock (initially) - Flushing Mode Selected on HS83121
[9 empty] | << | Interlock - Calibration Mode Selected on HS83121
[9 empty] | << | Interlock - If Manual Mode Selected on HS83121 AND Acid/Water Valve (VA83128) opened to acid then set to Dose position (open)
|  | ZZL83324 | Close Valve to Dose (Open Valve to Drain) |  | DO |  | Off | Close | << | Permissive (after initial opening) - Flushing Mode Selected on HS83121
|  | ZSH83324 | Valve to Dose Open Limit Switch |  | DI |  | Off | Open
|  | ZSL83324 | Valve to Dose Close (Valve to Drain Open) Limit Switch |  | DI |  | Off | Close
|  | ZIH83324 | Valve to Dose Open Indicator |  |  | DI | Off | Open |  |  |  | D | D |  | Yes
|  | ZIL83324 | Valve to Dose Close (Valve to Drain Open) Indicator |  |  | DI | Off | Close |  |  |  | D | D |  | No
|  | ZA83324 | Valve Fault |  |  | DI | Normal | Alarm | >> | Interlock - Inhibits or shutdown Operating Mode |  | D | D | Warning | Yes
83401 | Dosing Panel Area Safety Shower | FSH83401 | Flow Switch |  | DI |  | Alarm | Normal
|  | FAH83401 | Shower In Use Alarm |  |  | DI | Normal | Alarm |  | Alarms only if switch activates for 60 secs |  | D | D | Warning | Yes
83402 | Load-in Panel Area Safety Shower | FSH83402 | Flow Switch |  | DI |  | Alarm | Normal
|  | FAH83402 | Shower In Use Alarm |  |  | DI | Normal | Alarm |  | Alarms only if switch activates for 60 secs |  | D | D | Warning | Yes
83403 | Load-in Apron Area Safety Shower | FSH83403 | Flow Switch |  | DI |  | Alarm | Normal
|  | FAH83403 | Shower In Use Alarm |  |  | DI | Normal | Alarm |  | Alarms only if switch activates for 60 secs |  | D | D | Warning | Yes
83410 | Sampling Water Flow | FSL83410 | Low Flow Switch |  | DI |  | Alarm | Normal
|  | FAL83410 | Low Flow Alarm |  |  | DI | Normal | Alarm | >> | Interlock - If alarm activates for 15 minutes, initiates shutdown of Dosing system. |  |  | D | Critical | Yes
83411 | Treated Water Fluoride Concentration | AIT83411 | Fluoride Concentration Transmitter | Local | [6 empty] | D*
|  | AI83411 | Fluoride Concentration Indicator |  | AI
[6 empty] | AI | [5 empty] | D | D |  | Yes
|  | AAH83411 | High Fluoride Alarm |  |  | DI | Normal | Alarm |  |  |  | D | D | Warning | Yes
|  | AAHH83411 | High High Fluoride Alarm |  |  | DI | Normal | Alarm | >> | Initiates shutdown of Dosing system and changeover to standby system |  | D | D | Critical | Yes
|  | AAL83411 | Low Fluoride Alarm |  |  | DI | Normal | Alarm |  |  |  | D | D | Warning | Yes
|  | AALL83411 | Low Low Fluoride Alarm |  |  | DI | Normal | Alarm | >> | Initiates shutdown of Dosing system and changeover to standby system |  | D | D | Critical | Yes
* Direct "hard-wired" connection
Notes: | 1) It is recommended that ‘Flushing’, ‘Calibration’ and ‘Manual’ modes be selected and controlled only at the FLIP as onsite observation during operation of these modes would be required to minimise potential safety hazards.
Once the duty system has failed, it will be latched out and not be available for selection until the alarm condition is acknowledged and reset. Low clear water flow or dosing pump running underspeed will stop the dosing pump but not latch it out.