## FuncDescriptOverview
DS 73 Sodium Hypochlorite Design Standard - Functional Description Overview
Ver 1.2 - April 2023
Associated P&IDs: JD71-60-82.1 to JD71-60-82.4
Object No. | Asset / Process | P&ID Tag | Physical Description | Control / Interlock / Permissive |  | Location / Function C = Control, D = Display (LP) = Load-in Panel |  |  | Severity | Data Historian | I/O Type SM = Scada Master |  |  | State 0 | State 1
|  |  |  | ( >> triggers, << triggered by ) |  | Local | OIP | HMI |  | (Yes/No) | Local | PLC | SM
82101 | LOAD-IN DOOR | YI82101 | LOAD-IN DOOR OPEN INDICATION | >> | Flags that load-in door is open |  | D | D
|  | YS82101 | LOAD-IN DOOR SWITCH | >> | Interlock - When load-in door closes, YS82101 switch is activated triggering VA82105 to open to site drainage (and closed to Waste Holding Tank).
|  |  |  | >> | Interlock - When load-in door opens, YS82101 switch is de-activated triggering VA82105 to open to Waste Holding Tank (and closed to site drainage).
82104 | LOAD-IN APRON SUMP LEVEL | LSH82104 | HIGH LEVEL SWITCH
|  | LAH82104 | HIGH LEVEL ALARM | >> | Alerts that level in the sump is high. | D (LP) | D | D | Critical
82105 | LOAD-IN APRON SUMP VALVE | HS82105A | VALVE AUTO/MANUAL SELECTOR |  |  |  | C | C
| (3-WAY VALVE) | HS82105B | VALVE TO DRAINAGE / WASTE TANK SELECTOR |  |  |  | C | C
|  | ZZH82105 | OPEN VALVE TO DRAINAGE | << | Interlock - Activation of YS82101 from closing load-in door opens VA82105 to soakwell/site drainage (closed to Waste Holding Tank).
|  | ZZL82105 | OPEN VALVE TO WASTE HOLDING TANK (CLOSE TO DRAINAGE) | << | Interlock - De-activation of YS82101 from opening load-in door opens VA82105 to Waste Holding Tank (closed to soakwell/site drainage).
|  |  |  | << | Interlock - In event of power outage, VA82105 opens to Waste Holding Tank (closed to soakwell/site drainage).
|  | ZSH82105 | VALVE OPEN TO DRAINAGE LIMIT SWITCH
|  | ZSL82105 | VALVE OPEN TO WASTE HOLDING TANK LIMIT SWITCH
|  | ZIH82105 | VALVE OPEN TO DRAINAGE INDICATION |  |  | D (LP) | D | D
|  | ZIL82105 | VALVE OPEN TO WASTE HOLDING TANK INDICATION |  |  | D (LP) | D | D
|  | ZA82105 | VALVE FAULT | >> | Interlock - VA82105 opens to Waste Holding Tank (closed to soakwell/site drainage). |  | D | D | Urgent
82106 | BUND SUMP DRAIN VALVE | ZZH82106 | OPEN VALVE
|  | ZZL82106 | CLOSE VALVE | << | Interlock - Bund sump conductivity high alarm active.
|  |  |  | << | Interlock - Valve is timed to close after it is left open for 5 minutes continuously, whether override is selected or not.
|  | ZSH82106 | VALVE OPEN LIMIT SWITCH
|  | ZSL82106 | VALVE CLOSED LIMIT SWITCH
|  | ZIH82106 | VALVE OPEN INDICATOR |  |  |  | D | D
|  | ZIL82106 | VALVE CLOSE INDICATOR |  |  |  | D | D
|  | ZA82106 | VALVE FAULT | >> | Valve to be fail-close. |  | D | D | Warning
|  | HS82106A | VALVE MANUAL OVERRIDE SWITCH | >> | Permissive - Overrides valve VA82106 interlock at OIP |  | C
|  | HS82106B | VALVE MANUAL OPEN/CLOSE SWITCH | >> | Valve switch at OIP |  | C
|  | HS82106C | VALVE MANUAL OVERRIDE SWITCH | >> | Permissive - Overrides valve VA82106 interlock near valve | C
|  | HS82106D | VALVE MANUAL OPEN/CLOSE SWITCH | >> | Valve switch near valve | C
82107 | WASTE HOLDING TANK LEVEL | LSH82107 | HIGH LEVEL SWITCH
|  | LAH82107 | HIGH LEVEL ALARM | >> | Alerts operator to arrange for pumpout of waste holding tank. |  | D | D | Warning
82108 | LOAD-IN PANEL ALARM TEST SWITCH | HS82108 | ALARM TEST | >> | Switch to test integrity of all visual and audible alarms on Load-in Panel before load-in of chemical | C (LP)
82109 | LOAD-IN PANEL ALARM ACKNOWLEDGE SWITCH | HS82109 | ALARM ACKNOWLEDGEMENT | >> | Switch to acknowledge visual and audible alarms on Load-in Panel | C (LP)
82162 | HYPOCHLORITE TANKS GAS PURGE RETURN VALVES | ZA82162 | GAS RETURN VALVES NOT FULLY OPEN ALARM | >> | Permissive - If fully open signal are not present for both gas return valves VA82112 and VA82122, then the system loses its permissive to operate and shutdown of dosing system is initiated (if already operating) which will trigger a "Water Quality Breached" alarm. |  | D | D | Critical
82115 | HYPOCHLORITE TANK NO.1 LEVEL | LIT82115 | LEVEL TRANSMITTER |  |  | D
| (PRESSURE TRANSMITTER) | LI82115 | LEVEL INDICATOR | >> | Indication of hypochlorite level/volume in the tank no.1 | D (LP) | D | D
|  | LAH82115 | HIGH LEVEL ALARM | >> | Alerts delivery tanker driver to stop filling | D (LP) | D | D | Urgent
|  | LAL82115 | LOW LEVEL ALARM | >> | Alerts need to re-order chemical |  | D | D | Warning
|  | LALL82115 | LOW LOW LEVEL ALARM | >> | Interlock - Close tank isolation valve VA82137 and shut down duty Dosing Pump |  | D | D | Critical
82125 | HYPOCHLORITE TANK NO.2 LEVEL | LIT82125 | LEVEL TRANSMITTER |  |  | D
| (PRESSURE TRANSMITTER) | LI82125 | LEVEL INDICATOR | >> | Indication of hypochlorite level/volume in the tank no.2 | D (LP) | D | D
|  | LAH82125 | HIGH LEVEL ALARM | >> | Alerts delivery tanker driver to stop filling | D (LP) | D | D | Urgent
|  | LAL82125 | LOW LEVEL ALARM | >> | Alerts need to re-order chemical |  | D | D | Warning
|  | LALL82125 | LOW LOW LEVEL ALARM | >> | Interlock - Close tank isolation valve VA82147 and shut down duty Dosing Pump |  | D | D | Critical
82134 | HYPOCHLORITE TANK NO.1 LEVEL | LG82134 | MAGNETIC LEVEL GAUGE | >> | Provides local visual indication of the level in the tank no.1 | D (LP)
| (MAGNETIC LEVEL GAUGE) | LSHH82134 | HIGH HIGH LEVEL SWITCH (MAGNETIC)
|  | LAHH82134 | HIGH HIGH LEVEL ALARM (MAGNETIC) | >> | Alerts tank is close to overflowing, including audible alarm at Load-in Panel. Interlock - Isolates power supply to fill pump GPO | D (LP) | D | D | Critical
82144 | HYPOCHLORITE TANK NO.2 LEVEL | LG82144 | MAGNETIC LEVEL GAUGE | >> | Provides local visual indication of the level in the tank no.2 | D (LP)
| (MAGNETIC LEVEL GAUGE) | LSHH82144 | HIGH HIGH LEVEL SWITCH (MAGNETIC)
|  | LAHH82144 | HIGH HIGH LEVEL ALARM (MAGNETIC) | >> | Alerts tank is close to overflowing, including audible alarm at Load-in Panel. Interlock - Isolates power supply to fill pump GPO | D (LP) | D | D | Critical
82137 | HYPOCHLORITE TANK NO.1 OUTLET VALVE | HS82137A | VALVE AUTO/MANUAL SELECTOR |  |  |  | C | C
|  | HS82137B | VALVE MANUAL OPEN/CLOSE SWITCH |  |  |  | C | C
|  | ZZH82137 | OPEN VALVE
|  | ZZL82137 | CLOSE VALVE | << | Interlock - Valve closes when both Bund Sump Conductivity High Alarm (AAH82153) AND Bund Sump level High Alarm (LAH82152) activated.
|  |  |  | << | Interlock - Valve closes when Hypo Tank 1 level Low Low Alarm (LALL82115) activated.
|  | ZSH82137 | VALVE OPEN LIMIT SWITCH
|  | ZSL82137 | VALVE CLOSED LIMIT SWITCH
|  | ZIH82137 | VALVE OPEN INDICATOR |  |  |  | D | D
|  | ZIL82137 | VALVE CLOSE INDICATOR |  |  |  | D | D
|  | ZA82137 | VALVE FAULT | << | Valve failed to go to open/closed positions when called. |  | D | D | Urgent
|  |  |  | >> | Interlock - If Tank 2 outlet valve VA82147 is also closed or not available, initiates shutdown of dosing system and triggers "Water Quality Breached" alarm. |  | D | D | Critical
82147 | HYPOCHLORITE TANK NO.2 OUTLET VALVE | HS82147A | VALVE AUTO/MANUAL SELECTOR |  |  |  | C | C
|  | HS82147B | VALVE MANUAL OPEN/CLOSE SWITCH |  |  |  | C | C
|  | ZZH82147 | OPEN VALVE
|  | ZZL82147 | CLOSE VALVE | << | Interlock - Valve closes when both Bund Sump Conductivity High Alarm (AAH82153) AND Bund Sump level High Alarm (LAH82152) activated.
|  |  |  | << | Interlock - Valve closes when Hypo Tank 2 level Low Low Alarm (LALL82125) activated.
|  | ZSH82147 | VALVE OPEN LIMIT SWITCH
|  | ZSL82147 | VALVE CLOSED LIMIT SWITCH
|  | ZIH82147 | VALVE OPEN INDICATOR |  |  |  | D | D
|  | ZIL82147 | VALVE CLOSE INDICATOR |  |  |  | D | D
|  | ZA82147 | VALVE FAULT | << | Valve failed to go to open/closed positions when called. |  | D | D | Urgent
|  |  |  | >> | Interlock - If Tank 1 outlet valve VA82137 is also closed or not available, initiates shutdown of dosing system and triggers "Water Quality Breached" alarm. |  | D | D | Critical
82152 | BUND SUMP LEVEL | LSH82152 | HIGH LEVEL SWITCH
|  | LAH82152 | HIGH LEVEL ALARM | >> | No interlock if only high level alarm triggered |  | D | D | Warning
|  |  |  | >> | Interlock - IF Bund Sump Conductivity High Alarm AAH82153 activated at the same time, closes Hypo Tank outlet valves, which will initiates system shutdown and triggers "Water Quality Breached" alarm. |  | D | D | Critical
82153 | BUND SUMP CONDUCTIVITY | AIT82153 | CONDUCTIVITY TRANSMITTER |  |  | D
|  | AI82153 | CONDUCTIVITY INDICATOR |  |  |  | D | D
|  | AAH82153 | HIGH CONDUCTIVITY ALARM | >> | Indicates likely Hypo leak in bund. Interlock - closes Bund Sump Drain Valve VA82106 or prevents it from opening. |  | D | D | Urgent
|  | AAHH82153 | HIGH HIGH CONDUCTIVITY ALARM | >> | Interlock - IF Bund Sump Level High Alarm LAH82152 activated at the same time, closes Hypo Tank outlet valves, which will initiates system shutdown and triggers "Water Quality Breached" alarm. |  | D | D | Critical
82210 | HYPO DOSING PUMP NO. 1 | HS82210A | PUMP CONTROL AUTO / MANUAL SELECTOR |  |  |  | C | C
|  | HS82210B | MOTOR MANUAL START / STOP |  |  |  | C | C
|  | IY82210 | RUN MOTOR | << | Pump runs as part of Hypo Dosing system sequence. The pump speed is determined by pump controller algorithm (refer to Control Functional Specification) to provide the flow determined by the Hypo Dosing control loop FC82426.
|  |  |  | << | Interlock - Pump starts when the recipient water flow FIT XXXXX exceeds minimum flow set point Xm3/h.
|  |  |  | << | Pump stops as determined by pump controller algorithm and when Hypo Dosing system shuts down.
|  |  |  | << | Interlock - Pump stops when the recipient water flow FIT XXXXX falls below minimum flow set point Xm3/h (allow minimum run time of 2 mins if falls during dosing startup).
|  |  |  | << | Interlock - Pump stops when its speed falls below the set minimum pump speed (HC82210C)
|  | YS82210B | MOTOR RUNNING SWITCH | >> | Triggers the opening of degassing valve VA82221 for set duration when pump starts up and reaches full speed.
|  | YL82210 | MOTOR RUNNING STATUS LIGHT |  |  |  | D | D
|  | SC82210 | MOTOR SPEED CONTROLLER | >> | Provides speed adjustment to SY82210 as determined by Dosing Control Loop FC82426 flow paced from recipient main water flow FIT XXXXX
|  | SY82210 | MOTOR VARIABLE SPEED DRIVE | >> | Adjusts pump operating speed to the required flow rate
|  | SI82210 | PUMP SPEED INDICATOR |  |  |  | D | D
|  | HC82210B | PUMP SPEED MANUAL ADJUSTMENT | >> | Manual adjustment of Pump Speed |  | C | C
|  | HC82210C | MAXIMUM PUMP SPEED SETPOINT | >> | Data used to prevent Pump running overspeed |  | C | C
|  | YS82210A | PUMP WARNING
|  | YS82210C | MOTOR PROTECTION FAULT SWITCH
|  | YA82210A | MOTOR PROTECTION FAULT ALARM | >> | Interlock - Initiates shutdown of duty dosing system and changeover to standby system |  | D | D | Urgent
|  | YA82210B | PUMP FAULT ALARM | >> | Interlock - Initiates shutdown of duty dosing system and changeover to standby system |  | D | D | Urgent
|  | KQI82210 | MOTOR HOURS RUN |  |  |  | D | D
82221 | DEGASSING VALVE NO.1 | HS82221A | VALVE AUTO/MANUAL SELECTOR |  |  |  | C | C
|  | HS82221B | VALVE MANUAL OPEN/CLOSE SWITCH |  |  |  | C | C
|  | ZZH82221 | OPEN VALVE | << | Interlock - Valve opens for set duration (HC82221) upon dosing pump PU82210 start-up, running full speed.
|  |  |  | << | Interlock - Valve to open when dosing panel is taken off-line
|  |  |  | << | Interlock - Valve to open upon failure or power outage (fail open)
|  | ZZL82221 | CLOSE VALVE | << | Interlock - Valve closes after set opening duration (HC82221) at dosing pump PU82210 start-up.
|  | ZA82221 | VALVE FAULT | >> | Interlock - Initiates shutdown of duty dosing system 1 and changeover to standby system. |  | D | D | Urgent
|  | HC82221 | VALVE OPENING DURATION |  |  |  | C | C
82224 | HYPO DOSING FLOW METER NO.1 | FIT82224 | FLOW TRANSMITTER | >> | Monitors the hypo dosing flow rate from dosing pump. | D
|  | FI82224 | FLOW INDICATOR |  |  |  | D | D
|  | FQI82224 | TOTALISED FLOW |  |  |  | D | D
|  | FAL82224 | HYPO LOW FLOW ALARM (HYDRAULIC FAULT) | >> | Alarm when flow fell below setpoint for 10 secs. Interlock - Initiates shutdown of duty dosing system 1 and changeover to standby system |  | D | D | Urgent
|  | HS82224 | TOTAL FLOW RESET |  |  |  | C | C
|  | HC82224 | HYPO LOW FLOW RATE SETPOINT | >> | % of Required Hypo flow rate |  | C | C
82310 | HYPO DOSING PUMP NO. 2 | HS82310A | PUMP CONTROL AUTO / MANUAL SELECTOR |  |  |  | C | C
|  | HS82310B | MOTOR MANUAL START / STOP |  |  |  | C | C
|  | IY82310 | RUN MOTOR | << | Pump runs as part of Hypo Dosing system sequence. The pump speed is determined by pump controller algorithm (refer to Control Functional Specification) to provide the flow determined by the Hypo Dosing control loop FC82426.
|  |  |  | << | Interlock - Pump starts when the recipient water flow FIT XXXXX exceeds minimum flow set point Xm3/h.
|  |  |  | << | Pump stops as determined by pump controller algorithm and when Hypo Dosing system shuts down.
|  |  |  | << | Interlock - Pump stops when the recipient water flow FIT XXXXX falls below minimum flow set point Xm3/h (allow minimum run time of 2 mins if falls during dosing startup).
|  |  |  | << | Interlock - Pump stops when its speed falls below the set minimum pump speed (HC82310C)
|  | YS82310B | MOTOR RUNNING SWITCH | >> | Triggers the opening of degassing valve VA82321 for set duration when pump starts up and reaches full speed.
|  | YL82310 | MOTOR RUNNING STATUS LIGHT |  |  |  | D | D
|  | SC82310 | MOTOR SPEED CONTROLLER | >> | Provides speed adjustment to SY82310 as determined by Dosing Control Loop FC82426 flow paced from recipient main water flow FIT XXXXX
|  | SY82310 | MOTOR VARIABLE SPEED DRIVE | >> | Adjusts pump operating speed to the required flow rate
|  | SI82310 | PUMP SPEED INDICATOR |  |  |  | D | D
|  | HC82310B | PUMP SPEED MANUAL ADJUSTMENT | >> | Manual adjustment of Pump Speed |  | C | C
|  | HC82310C | MAXIMUM PUMP SPEED SETPOINT | >> | Data used to prevent Pump running overspeed |  | C | C
|  | YS82310A | PUMP WARNING
|  | YS82310C | MOTOR PROTECTION FAULT SWITCH
|  | YA82310A | MOTOR PROTECTION FAULT ALARM | >> | Interlock - Initiates shutdown of duty dosing system 2 and changeover to standby system |  | D | D | Urgent
|  | YA82310B | PUMP FAULT ALARM | >> | Interlock - Initiates shutdown of duty dosing system 2 and changeover to standby system |  | D | D | Urgent
|  | KQI82310 | MOTOR HOURS RUN |  |  |  | D | D
82321 | DEGASSING VALVE NO.2 | HS82321A | VALVE AUTO/MANUAL SELECTOR |  |  |  | C | C
|  | HS82321B | VALVE MANUAL OPEN/CLOSE SWITCH |  |  |  | C | C
|  | ZZH82321 | OPEN VALVE | << | Interlock - Valve opens for set duration (HC82321) upon dosing pump PU82310 start-up, running full speed.
|  |  |  | << | Interlock - Valve to open when dosing panel is taken off-line
|  |  |  | << | Interlock - Valve to open upon failure or power outage (fail open)
|  | ZZL82321 | CLOSE VALVE | << | Interlock - Valve closes after set opening duration (HC82321) at dosing pump PU82310 start-up.
|  | ZA82321 | VALVE FAULT | >> | Interlock - Initiates shutdown of duty dosing system 2 and changeover to standby system. |  | D | D | Urgent
|  | HC82321 | VALVE OPENING DURATION |  |  |  | C | C
82324 | HYPO DOSING FLOW METER NO.2 | FIT82324 | FLOW TRANSMITTER | >> | Monitors the hypo dosing flow rate from dosing pump. | D
|  | FI82324 | FLOW INDICATOR |  |  |  | D | D
|  | FQI82324 | TOTALISED FLOW |  |  |  | D | D
|  | FAL82324 | HYPO LOW FLOW ALARM (HYDRAULIC FAULT) | >> | Alarm when flow fell below setpoint for 10 secs. Interlock - Initiates shutdown of duty dosing system 2 and changeover to standby system |  | D | D | Urgent
|  | HS82324 | TOTAL FLOW RESET |  |  |  | C | C
|  | HC82324 | HYPO LOW FLOW RATE SETPOINT | >> | % of Required Hypo flow rate |  | C | C
82406 | SAMPLE WATER PUMP | HS82406A | PUMP CONTROL AUTO / MANUAL SELECTOR |  |  |  | C | C
|  | HS82406B | MOTOR MANUAL START / STOP |  |  |  | C | C
|  | IY82406 | RUN MOTOR
|  | YS82406A | MOTOR RUNNING SWITCH
|  | YS82406B | MOTOR PROTECTION FAULT SWITCH
|  | YL82406 | MOTOR RUNNING STATUS LIGHT |  |  |  | D | D
|  | YA82406 | MOTOR PROTECTION FAULT ALARM | >> | Interlock - Dosing control continues with flow pacing based on last recorded chlorine residual. |  | D | D | Critical
|  | KQI82406 | MOTOR HOURS RUN
82418 | SAMPLE WATER FLOW | FI82418 | FLOW INDICATION | >> | Rotameter displays sample water flow. | D
|  | FSL82418 | LOW FLOW SWITCH | >> | Interlock - When switch is activated, dosing control will continue with flow pacing based on last recorded chlorine residual.
|  |  |  | >> | Interlock - If flow is restored within 15 min, allow flow to stabilise for 10 min before reverting dosing control to flow paced with residual trim.
|  | FAL82418 | LOW FLOW ALARM | << | FAL82418 alarm raised if flow not restored after 15 min. |  | D | D | Critical
82419 | CHLORINE RESIDUAL ANALYSIS | AIT82419 | CHLORINE RESIDUAL TRANSMITTER |  |  | D
|  | AI82419 | CHLORINE RESIDUAL INDICATION |  |  |  | D | D
|  | AAH82419 | CHLORINE RESIDUAL HIGH ALARM | >> | Interlock - If chlorine residual registered above high SP continuously for 6 min (configurable), initiates alarm and the changeover to standby dosing panel. If chlorine residual still stays above high level SP after changeover, HMI alarm would remain active, but no further changeover would occur. |  | D | D | Warning
|  | AAHH82419 | CHLORINE RESIDUAL HIGH HIGH ALARM | >> | Interlock - If chlorine residual registered above HH SP continuously for 1 min after changeover, initiates alarm (latched) and system shutdown. After 30 secs, triggers "Water Quality Breached" alarm and initiate shutdown of main water source. |  | D | D | Critical
|  | AAL82419 | CHLORINE RESIDUAL LOW ALARM | >> | Interlock - If chlorine residual registered below low SP continuously for 6 min (configurable), initiates alarm and the changeover to standby dosing panel. If chlorine residual still stays below low level SP after changeover, HMI alarm would remain active, but no further changeover would occur. |  | D | D | Warning
|  | AALL82419 | CHLORINE RESIDUAL LOW LOW ALARM | >> | Interlock - If chlorine residual registered below LL SP continuously for 1 min after changeover, initiate alarm (latched) and system shutdown. After 30 secs, triggers "Water Quality Breached" alarm and initiate shutdown of main water source. |  | D | D | Critical
|  | YA82419 | CHLORINE RESIDUAL ANALYSER FAILURE | >> | Interlock - If activated, dose flow control will continue with flow pacing based on last recorded chlorine residual. |  | D | D | Critical
|  | AC82419 | CHLORINE RESIDUAL CONTROLLER | >> | Output the required chlorine dose rate (trim adjustment) to FC82426 to achieve target chlorine residual setpoint HC82419A.
|  | QAH82419 | REQUIRED DOSE RATE HIGH ALARM | >> | Alarm to flag possible problem with the dosing process (issues with chlorine demand, hypo strength or analyser). No interlock. |  | D | D | Urgent
|  | QAL82419 | REQUIRED DOSE RATE LOW ALARM | >> | Alarm to flag possible problem with the dosing process (issues with chlorine demand, hypo strength or analyser). No interlock. |  | D | D | Urgent
|  | HC82419A | CHLORINE RESIDUAL SETPOINT | >> | Target chlorine residual setpoint in 'Auto Trim' control mode. |  | C | C
|  | HC82419B | UPPER DOSE RATE LIMIT | >> | Input QAH82419 setpoint value, normally set as 0.2 mg/L above normal steady state dose rate (0.2 + demand + target SP). |  | C | C
|  | HC82419C | LOWER DOSE RATE LIMIT | >> | Input QAL82419 setpoint value, normally set as 0.3 mg/L above normal steady state dose rate minus the target setpoint (0.3 + demand). |  | C | C
|  | HC82419D | HIGH CHLORINE RESIDUAL OFFSET | >> | Input offset value to add to target chlorine residual setpoint HC82419A to give AAH82419 trigger setpoint. |  | C | C
|  | HC82419E | LOW CHLORINE RESIDUAL OFFSET | >> | Input offset value to subtract from target chlorine residual setpoint HC82419A to give AAL82419 trigger setpoint. |  | C | C
|  | HC82419F | HIGH HIGH CHLORINE RESIDUAL SETPOINT | >> | Input AAHH82419 setpoint value, normally as per site Water Safety Plan (WSP). |  | C | C
|  | HC82419G | LOW LOW CHLORINE RESIDUAL SETPOINT | >> | Input AALL82419 setpoint value, normally 0.2 mg/L. |  | C | C
82426 | DOSING FLOW CONTROL | HS82426 | DOSE MODE (AUTO TRIM / FIXED) SELECTOR | >> | Switch to select 'Auto Trim' or 'Fixed' dose control mode. |  | C | C
|  | HC82426A | FIXED MODE DOSE RATE INPUT | >> | Input fixed dose rate value (mg/L) for ratio control flow paced hypo dosing in Fixed control mode. |  | C | C
|  | HC82426B | SODIUM HYPO STRENGTH INPUT | >> | Input Hypo strength in %w/v for calculating Hypochlorite dosing flow rate. |  | C | C
|  | FC82426 | FLOW CONTROLLER | >> | Provides dose flow adjustment to duty pump speed controller SC82210 / SC82310 to achieve required chlorine residual, normally with PID 'Auto Trim' chlorine dose rate adjustment from AC82419. In 'Fixed' mode, FC82426 flow adjustment is to fixed dose rate HC82426.
82428 | SAFETY SHOWER AND EYE WASH (LOAD-IN AREA) | FSH82428 | WATER FLOW SWITCH
|  | FAH82428 | IN USE INDICATION/ALARM | >> | Alarm triggered only if switch is activated for more than 60 seconds |  | D | D | Critical
82431 | SAFETY SHOWER AND EYE WASH (DOSING PANEL AREA) | FSH82431 | WATER FLOW SWITCH
|  | FAH82431 | IN USE INDICATION/ALARM | >> | Alarm triggered only if switch is activated for more than 60 seconds |  | D | D | Critical
Note on F98: Damon Howes: Please review and align with FCS text. Shutdowns should not occur until HH is reached. High provides pre-warning to operator.