|  |
| --- |
| **INSPECTION TEST AND PLAN EXAMPLE: A1, F1** |
| **Contractor/customer:**  ABBC Engineering | **Date of issue: 1st July 2021** |
| **Project title:** Karratha Tank Renew | **Prepared by: Joe Bloggs**  |
| **Water Corporation project No.:**  CW 1999999 | **Job/contract number: xxxxxxxxx** |
| **Description and system:**  Clarifier Internal Coatings System A1 F1  | **No. of pages: 3** |
| **Legend of inspection points:**

|  |
| --- |
|  **H = Hold Point.** Work may not proceed without approval or notification, unless approved by the principal or contractor.  **W = Witness Point.** Work may proceed without the presence of the principal. **S = Surveillance.** Witness at random, no formal notification required. **V = Verify.** **R/A = Review.** Review documents & accept.**(work can proceed if Principal cannot attend hold point inspection within three hours of notified time for attendance)** |

 |

| **N0** | **Activity/Operation** | **Specification/Document**  | **Acceptable Criteria** | **Verifying Document**  | **Person Responsible** | **Inspection & Verification Points** |
| --- | --- | --- | --- | --- | --- | --- |
| **Sub-****Contractor** | **Sign** | **Contractor** | **Sign** | **Principal or Nominee** | **Sign** |
| 1 | Review Client Specifications | * Water Corporation DS95
* Specification A1
* Specification F1
 | Read and fully understand the requirements & responsibilities.  | Signed and approved ITP | QC Inspector | **R/A** |  | **R/A** |  | **V** |  |
| 2 | Blasting and coating applicators qualification | * Water Corporation DS95
* ASTM D4228
 | As per coating contractor’s internal procedure and standards. | Verification of competency record (VOC) | QC Inspector | **H** |  | **V** |  | **V** |  |
| 3 | Certificate of inspection personnel | * Water Corporation DS95
* NACE/ACA
 | Certified as per specification requirements. | NACE/ACA | QC Inspector | **H** |  | **H** |  | **W** |  |
| 4 | Calibration of all test equipment | * Water Corporation DS 95
* SSPC PA2
* AS3894.3
* ISO 17025
 | Equipment manufacturers criteria, qualified person, or NATA registered or equivalent testing facility. | Calibration and testing certificates and records. | QC Inspector | **V** |  | **V** |  | **W** |  |
| 5 | Substrate inspection  | * Water Corporation DS 95
* Specification A1
 | Surfaces checked for no sharp edges, have a 2mm radius, and weld spatter burrs, etc. are removed. | Daily coating and inspection report | Supervisor/ QC Inspector | **H** |  | **W** |  | **W** |  |
| 6 | Surface cleanliness | * SSPC SP1
* AS3894.6
* AS1627.1
 | Oil, grease, dirt, and other foreign matter shall be removed. | Daily inspection report | Supervisor/ QC Inspector | **H** |  | **W** |  | **W** |  |
| 7 | Compressed air supply and clean air inspection | * ASTM D 4285-83
 | Compressed air shall be free from water and oil and tested each day. | Daily coating and inspection report | Supervisor/ QC Inspector | **V** |  | **S** |  | **W** |  |
| 8 | Verify abrasive blast and surface profile. | * Water Corporation DS 95
* Specification A1
* AS 1627.4
* AS 3894.5
* AS3894.12
 | Class 3 (white metal) finish.SSPC-SP 5, SA-3.Surface profile as per coating manufacturers recommendation, typically 75-100µm. | Daily coating and inspection report | QC Inspector | **H** |  | **S** |  | **S** |  |
| 8 | Test for chloride contamination | * Water Corporation DS 95
* Specification A1
* AS 3894.6
 | Immersion service -< 3µg/cm².Ambient service – < 5µg/cm². | Daily coating and inspection report | QC Inspector | **H** |  | **S** |  | **S** |  |
| 9 | Test for particulate surface contamination | * Water Corporation DS 95
* Specification A1
* AS 3894.6
* ISO 8502-3
 | Determination of surface dust pressure sensitive tape method.Dust level shall not exceed rating 2. | Daily coating and inspection report | QC Inspector | **V** |  | **W** |  | **S** |  |
| 10 | Ambient conditions | * Water Corporation DS 95
* Specification A1
* Specification F1
* AS3894.7
* AS3894.13
 | Ambient conditions shall be recorded at least 4 times per shiftMax relative humidity 85%Min/Max substrate Temp 10°C - 55°CMin Substrate Temp 3oC above dew point. | Daily coating and inspection report | QC Inspector  | **H** |  | **W** |  | **W** |  |
| 11 | Stripe coat 1st and 2nd coating. | * Water Corporation DS 95
* Water Corporation F1
 | Ensure all welds, edges, crevices, seams, joints, and corners are brush stripe coated on each application. | Daily coating and inspection report | QC Inspector | **V** |  | **W** |  | **W** |  |
| 12 | Apply 1st coat **Insert the Coating Product Name** | * Water Corporation DS 95
* Water Corporation F1
 | Monitor WFT/DFT regularly during and after application. 500 µm DFT minimum | Daily coating and inspection report | QC Inspector | **V** |  | **W** |  | **W** |  |
| 13 | Apply 2nd coat **Insert the Coating Product Name** | * Water Corporation DS 95
* Water Corporation F1
 | Monitor WFT regularly during application. To achieve a **total** **minimum DFT of 1000µm** | Daily coating and inspection report | QC Inspector | **V** |  | **W** |  | **W** |  |
| 14 | Finish coat inspection | * Water Corporation DS 95
* Specification F1
* AS3894.3
* AS3894.4
* SSPC PA2
 | Visual inspection for runs, sags and any inclusions etc.Coating cured and final DFT recorded. All batch numbers are documented.  | Daily coating and inspection report | QC Inspector | **H** |  | **H** |  | **W** |  |
| 15 | Holiday testing for buried, immersion or as defined in the ITP. | * Water Corporation DS 95
* AS 3894.1
* Or manufacturers recommendation.
 | 100% of total coated accessible surface area. | Daily coating and inspection report | Supervisor / Inspector | **H** |  | **H** |  | **H** |  |
| 16 | Adhesion testing on test panel. | * Water Corporation DS 95
* Specification F1
* AS3894.9
 | Adhesion test of cured coating on test panel. (Pull off test) As per Manufacturers recommendations. | Daily coating and inspection report | Supervisor / Inspector | **H** |  | **H** |  | **H** |  |
| 17 | Verifying acceptancedocumentation. | * Water Corporation DS 95
* AS3894.12
 | Check that all inspection, test documentation and completion reports have been completed and singed. Submit documentation to Contractor/Principal. | Completion report.IRC and signed ITP. | Inspector / Principal | **H/R** |  | **RA** |  | **RA** |  |
| **COMMENTS AND NOTES:** |
| **Sub-contractor, contractor then principal to sign ITP at completion of works and ITP close out.** |
|  |
|  |

|  |  |  |  |  |
| --- | --- | --- | --- | --- |
| **ITP Approved and accepted** | **Name** | **Position** | **Signature** | **Date** |
|  |  |  |  |  |
|  |  |  |  |  |
| **Water Corporation** |  |  |  |  |