This form shall be completed as shown. The completed form should accompany any specification or scope of work document for the programming and SCADA implementation.  The form provides the required information for the configuration of the UWSS mimics and code.

The form is designed such that individual sections are completed as the project progresses by the appropriate person as indicated.  When the project is completed the form, along with required documentation is to be sent to the relevant persons at the Water Corporation for incorporation into project files (see Section 5).

| SECTION 1: THIS SECTION TO BE COMPLETED AT START OF PROJECT BY SCADA DESIGN ADVISOR WITH INPUT FROM REGION AND/OR DESIGN MANAGER |
| --- |
| Project Name: |  | Project Code (If WC project): |  |
| Project Manager: |  | Contact Number: |  |
| Project Contact: |  | Contact Number: |  |
| SCADA Design Engineer (if WC Project): |  | Contact Number: |  |
| Brief Description of Project: |
| SITE DETAILS |
| Site Name |  | Region |  |
| Address |  | District |  |
| Functional Location (SAP) |  | Scheme/Town |  |
| If this is a small two pump WWPS site, unless otherwise specified, then use WORM I/O list. If not WORM then use WWPS01 I/O list. |
| Is this a “Critical” Site? See Note 1 | Y/N |
| CONFIGURATION VALUES |
| Action on Communications Failure | Fail Safe Stop: Required/ Not Required |

# Note 1   WWPSs are defined as “Critical” for the purposes of SCADA requirements if they fall in to the category of Highly Sensitive or Sensitive on the basis of their overflow receiving environment as defined below:

Highly Sensitive:	Dry-season pools in intermittent creeks and rivers, wetland and/or high potential for health or loss of amenity impact.

Sensitive: 	Permanent creek, river, wet compensating basin with ecological value and lakes and/or intermediate potential for impact on health or amenity.

NB: The sensitive areas described in Design Manual DS51 Clause 4.10 (k) would fit these categories

For completeness non-critical receiving environments are described below:

Moderate Sensitivity:	Water Corporation and Council Drains, water protection areas and/or low potential for impact on health or amenity

Low Sensitivity:	Water Corp Comp basins with no ecological value, dry creeks, sumps, roadway, ground only and/or low potential for impact on health or amenity.

| SECTION 2 THIS SECTION TO BE COMPLETED AT CONCEPT/ ENGINEERING DESIGN STAGE BY THE SCADA DESIGN ADVISOR WITH INPUT FROM THE MECH./ CIVIL ENGINEER |
| --- |
| CONFIGURATION VALUES |
| Wet Well Top of Slab | m RL |
| Duty Pump Start Setpoint (Distance from top of slab) |  |
| Standby(Changeover) Pump Start Setpoint (Distance from top of slab) |  |
| Duty / Standby (Changeover) Pump Stop Setpoint (Distance from top of slab) |  |
| Invert of Inlet Level (Distance from top of slab) |  |
| High Float Switch Level (Distance from top of slab) See Note 2 |  |
| Flow to Storage Float Switch Level (Distance from top of slab) See Note 2 |  |
| Emergency Storage in Use Float Switch Level (Distance from top of slab)(Captive Storage only) See Note 2 |  |
| Half Storage Float Switch Level (Distance from top of slab) See Note 2 |  |
| Overflow to Environment (Distance from top of slab) See Note 2 |  |
| Is there an associated Remote Emergency Overflow to the Environment to be shown | Y/N If Yes, what address? |
| Is this a Dry Well site? | Y/N |
| Is this a Split Wet Well? | Y/N |
| Name of WWPS Immediately Upstream (where applicable) |  |
| Name of WWPS Immediately Downstream (where applicable) |  |
| Peer Inhibits Required to be sent (other pump stations which need to be stopped if this pump station is stopped) (WORM sites only) | Y/N If Yes, then attach list of pump station/s: |
| Peer Inhibits Received (other pump stations which if are stopped will require this pump station to be stopped) (WORM sites only) | Y/N If Yes, then attach list of pump station/s: |
| Is this the Master for any Master/Slave Inhibits? (WORM sites only) | Y/N If Yes, then attach list of pump station/s inhibited: |
| Is this the Slave for any Master/Slave Inhibits? (WORM sites only) | Y/N If Yes, then which pump station is the Master?: |
| Emergency Generator Installed | Y/N |

Note: The word Standby is used in WWPS01 code and Changeover is used in WORM code.

| Instrument Ranges |
| --- |
| Signal | Range | Units |
| Delivery Pressure (Required only on Special Request) |  | m |
| Flow Rate |  | l/s |
| Motor Current |  | A |
| Motor Power (Required only for Motors sized > 45kW) |  | kW |
| Well Level |  | m |

# Note 2   These values are the equivalent level in the well for the float switches (that is, if the switch is located external to the well, then it is the level reading in the well at which point the switch should be activated).  The values are used to calculate the “Level Discrepancy Alarm”.  The “Level Discrepancy Alarm” is activated if the level reading in the well is not within a range to match these float switch values.

“Emergency Storage in Use” float switch is not required if the emergency storage is self draining.

| SECTION 3 (continued) THIS SECTION TO BE COMPLETED AT CONCEPT/ ENGINEERING DESIGN STAGE BY THE SCADA DESIGN ADVISOR WITH INPUT FROM THE MECH./ CIVIL ENGINEER |
| --- |
| SITE CO-ORDINATES (Conforming to MGA) |
| Zone (eg 50, 51): | Easting: | Northing: |
| UWSS CONNECTION (How is this site connected to the UWSS) |
| Communications Type Notes: PI Data Historian configuration to be included If PS is WWPS01 & non critical then there must be an IP main communications medium selected , backup communications medium is optional If PS is “Critical” (WORM or WWPS01) then there must be an IP main and a backup communications medium selected If PS is “WORM” and non critical then there must be an IP main communications and IP backup communications medium is optional. Router is required when both main & backup communications are used. |
| ADSL (IP)/NBN (IP) (LTM/PTM form to be submitted to ICT SCADA Coordinator) (ADSL/NBN Feasibility required) | Main/Backup (select) |
| Cellular (IP) (LTM/PTM form to be submitted to ICT SCADA Coordinator) (Cellular Testing to be completed) | Main/Backup (select) |
| Satellite (IP) Consult SCADA Advisor if this is required. (LTM/PTM form to be submitted to ICT SCADA Coordinator) (Satellite Testing to be completed) | Backup |
| Radio (IP) Consult SCADA Advisor if this is required. (Radio Design Report required) | Main/Backup (select) |
| HARDWARE |
| RTU Required: | Schneider SCADAPack TBUP575-UA56-AB00S, Schneider Expansion Module 6601 TBUX297583S, Schneider Expansion Module 5414 TBUX297378. See note 3 |

| DRAWINGS/REPORTS TO BE ATTACHED |
| --- |
| Site Layout | Document Number: |
| SCADA Block Diagram | Document Number: |
| Radio Final Design Report | Document Number: |
| Cellular Final Design Report | Document Number: |

Note 3: WORM build will require 575 unit & both 6601 & 5414 expansion modules, WWPS01 will only require 575 and 6601 units.

| SECTION 4: THIS SECTION TO BE COMPLETED AT CONCEPT/ ENGINEERING DESIGN STAGE BY SCADA DESIGN ADVISOR |
| --- |
| CONFIGURATION VALUES |
| Flow Pulse Value (Required only for Sites with Hard-wired Flow Pulse Input such as WORM sites. Serial link to Flowmeter preferred, where Available and non WORM sites.) | Default = 0.1 kl/pulse |
| kWh Pulse Value (Required only for Sites with Maximum Pumping Power > 15kW) | Default = 0.01 kWh /pulse for direct current meters Default = 0.0625 kWh /pulse for CT meters |
| kVARh Pulse Value (Required only for Sites with Maximum Pumping Power > 15kW) | Default = 0.01 kVARh /pulse for direct current meters Default = 0.0625 kVARh /pulse for CT meters |
| Permanent Emergency Generator Installed | Y/N |
| No of Pumps Allowed to Run Simultaneously | 1 / 2 Default =1 , If =2 then WORM not applicable |
| Low Flow Pump Trip Value | Default = 10% of flow range |
| Low Current Pump Alarm Value | Default = 20% of current range |
| Float Tolerance | Default = 2% of level range |
| Level Minimum Change (to detect faults) | Default = 2% |
| On Peak Time Minutes (time during which if level does not change an alarm will get raised) | Default = 30 |
| Off Peak Time Minutes (time during which if level does not change an alarm will get raised) | Default = 60 |
| RADIO- ACMA LICENCE DETAILS (Note: Cellular is the preferred communications medium) (To be obtained from SCADA Branch, Principal SCADA Capability) |
| Licence No: |  | Spectrum Access No: |  |
| DRAWINGS/REPORTS TO BE ATTACHED |
| I/O List (Update list at end of this form) |  |

SECTION 5 THIS SECTION TO BE COMPLETED AT END OF PROJECT BY MAIN CONTRACTOR

FORM COMPLETION AND SUBMISSION

At the completion of the Project, the following information shall be submitted to the Project Manager and the software loaded onto Autosave@watercorporation.com.au

This form F40-01 with all attachments

Electronic copies of RTU Remote Connect code and RTU Config code

SECTION 6 THIS SECTION TO BE COMPLETED IF REQUIRED

SITE SPECIFIC SPECIAL REQUIREMENTS

# Physical I/O List for Standard Wastewater Pump Station

The lists below show the full complement of physical I/O generally assigned for Wastewater Pump Stations. This includes both the WWPS01 & WORM sites. The standard I/O list for the applicable type shall be used. Not all of the I/O is applicable for each site, for example, not all pump stations require a generator.  Indicate which signals are required/not required by selecting a “Yes” or No” under the “Used” column for that signal.

Also, note the following:

- For pumps >45kW, individual pump powers shall be monitored in addition to individual pump currents

- For pump stations with a maximum pumping power > 15kW, kWh meter monitoring shall be used.

WWPS01 I/O List

| Description | Input/Output Type | P&ID Tag | Units | Used | Point No |
| --- | --- | --- | --- | --- | --- |
| Site Power Healthy | Physical Digital Input |  |  | Yes | 1 |
| Security Healthy | Physical Digital Input |  |  | Yes | 2 |
| Site kWh Totalisation Pulse | Physical Digital Input |  |  | Yes/No | 3 |
| Site kVARh Totalisation Pulse | Physical Digital Input |  |  | Yes/No | 4 |
| Site Power End of Interval Pulse | Physical Digital Input |  |  | Yes/No | 5 |
| Battery Charger Supply Healthy | Physical Digital Input |  |  | Yes | 6 |
| Station Manhole Normal | Physical Digital Input |  |  | Yes | 7 |
| Flow Totalisation Pulse See Note 4 | Physical Digital Input |  |  | Yes/No | 8 |
| Pump 1 On Normal (IED Control Enabled) | Physical Digital Input |  |  | Yes | 9 |
| Pump 1 Running | Physical Digital Input |  |  | Yes | 10 |
| Pump 1 Available | Physical Digital Input |  |  | Yes | 11 |
| Pump 1 Motor Protection Fault | Physical Digital Input |  |  | Yes | 12 |
| Pump 1 Motor Thermistor Fault | Physical Digital Input |  |  | Yes | 13 |
| Pump 1 Starter Thermistor Fault | Physical Digital Input |  |  | Yes/No | 14 |
| Local Inhibit Override | Physical Digital Input |  |  | Yes | 15 |
| Test Duty Pump | Physical Digital Input |  |  | Yes | 16 |
| Duty Selector Switch Bit 1 | Physical Digital Input |  |  | Yes | 17 |
| Duty Selector Switch Bit 2 | Physical Digital Input |  |  | Yes | 18 |
| Local Reset | Physical Digital Input |  |  | Yes | 19 |
| Dry Well OK | Physical Digital Input |  |  | Yes/No | 20 |
| Wet Well Level Not High | Physical Digital Input |  |  | Yes | 21 |
| Wet Well Level Not Emergency Storage In Use | Physical Digital Input |  |  | Yes | 22 |
| Wet Well Level Not Half Storage | Physical Digital Input |  |  | Yes | 23 |
| Wet Well Level Not Overflow | Physical Digital Input |  |  | Yes | 24 |
| Pump 2 On Normal (IED Control Enabled) | Physical Digital Input |  |  | Yes | 25 |
| Pump 2 Running | Physical Digital Input |  |  | Yes | 26 |
| Pump 2 Available | Physical Digital Input |  |  | Yes | 27 |
| Pump 2 Motor Protection Fault | Physical Digital Input |  |  | Yes | 28 |
| Pump 2 Motor Thermistor Fault | Physical Digital Input |  |  | Yes | 29 |
| Pump 2 Starter Thermistor Fault | Physical Digital Input |  |  | Yes/No | 30 |
| Generator Running | Physical Digital Input |  |  | Yes/No | 31 |
| Generator Fault | Physical Digital Input |  |  | Yes/No | 32 |
| Pump 1 Start Request | Physical Digital Output |  |  |  | 1 |
| Pump 1 Hydraulic Fault | Physical Digital Output |  |  |  | 2 |
| Pump 1 Electrical Fault | Physical Digital Output |  |  |  | 3 |
| Pump 1 Inhibited | Physical Digital Output |  |  |  | 4 |
| Pump 1 Motor Protection Fault Reset | Physical Digital Output |  |  |  | 5 |
| Command to Run on Battery | Physical Digital Output |  |  |  | 6 |
| Pump Station Called | Physical Digital Output |  |  |  | 7 |
| Telemetry Failure Indication | Physical Digital Output |  |  |  | 8 |
| Pump 2 Start Request | Physical Digital Output |  |  |  | 9 |
| Pump 2 Hydraulic Fault | Physical Digital Output |  |  |  | 10 |
| Pump 2 Electrical Fault | Physical Digital Output |  |  |  | 11 |
| Pump 2 Inhibited | Physical Digital Output |  |  |  | 12 |
| Pump 2 Motor Protection Fault Reset | Physical Digital Output |  |  |  | 13 |
|  | Physical Digital Output |  |  |  |  |
|  | Physical Digital Output |  |  |  |  |
| Standby Latched | Physical Digital Output |  |  |  | 16 |
| Well Level | Physical 32 bit Analog Input |  | m | Yes | 1 |
| Delivery Pressure | Physical 32 bit Analog Input |  | m | Yes/No | 2 |
|  | Physical 32 bit Analog Input |  |  |  |  |
| Flow Rate See Note 4 | Physical 32 bit Analog Input |  | L/s | Yes/No | 4 |
| Pump 1 Power | Physical 32 bit Analog Input |  | kW | Yes/No | 5 |
| Pump 1 Current | Physical 32 bit Analog Input |  | A | Yes/No | 6 |
|  | Physical 32 bit Analog Input |  |  |  | 7 |
|  | Physical 32 bit Analog Input |  |  |  | 8 |
|  | Physical 32 bit Analog Input |  |  |  | 9 |
|  | Physical 32 bit Analog Input |  |  |  | 10 |
| Pump 2 Power | Physical 32 bit Analog Input |  | kW | Yes/No | 11 |
| Pump 2 Current | Physical 32 bit Analog Input |  | A | Yes/No | 12 |

Note 4	For non WORM sites flow rate and flow total signals may also be obtained via serial link, where available.

WORM I/O List

| Description | Input/Output Type | P&ID Tag | Units | Used | Point No |
| --- | --- | --- | --- | --- | --- |
| BASE UNIT 575 |  |  |  |  |  |
| Site Power Healthy | Physical Digital Input |  |  | Yes | 1 |
| Local Reset | Physical Digital Input |  |  | Yes | 2 |
| Not Flow to Emergency Storage | Physical Digital Input |  |  | Yes/No | 3 |
| Not Emergency Storage in Use | Physical Digital Input |  |  | Yes/No | 4 |
| Not Half Storage | Physical Digital Input |  |  | Yes | 5 |
| Not Overflow to the Environment | Physical Digital Input |  |  | Yes | 6 |
| Dry Well Not Flooded | Physical Digital Input |  |  | Yes/No | 7 |
|  | Physical Digital Input |  |  |  | 8 |
| Unit 1 Normal | Physical Digital Input |  |  | Yes | 9 |
| Unit 1 Running | Physical Digital Input |  |  | Yes | 10 |
| Unit1 Available | Physical Digital Input |  |  | Yes | 11 |
| Unit 1 Motor Overload | Physical Digital Input |  |  | Yes | 12 |
| Unit 1 Motor Over temperature | Physical Digital Input |  |  | Yes | 13 |
| Unit 1 Stator Leakage | Physical Digital Input |  |  | Yes/No | 14 |
| Unit 1 Starter Over temperature | Physical Digital Input |  |  | Yes/No | 15 |
|  | Physical Digital Input |  |  |  | 16 |
| Power Supply Monitor | RS485 Modbus Port 4 |  |  | Yes/No |  |
| EXPANSION MODULE 6601 |  |  |  |  |  |
| Security Healthy | Physical Digital Input |  |  | Yes | 1 |
| DC UPS Healthy | Physical Digital Input |  |  | Yes | 2 |
|  | Physical Digital Input |  |  |  | 3 |
| On Peak Tariff | Physical Digital Input |  |  | Yes/No | 4 |
| Flow Totalisation Pulse see Note 5 | Physical Digital Input |  |  | Yes/No | 5 |
| Site kWh Pulse | Physical Digital Input |  |  | Yes/No | 6 |
| Site kVARh Pulse | Physical Digital Input |  |  | Yes/No | 7 |
| End of Interval Pulse | Physical Digital Input |  |  | Yes/No | 8 |
| Unit 2 Normal | Physical Digital Input |  |  | Yes | 9 |
| Unit 2 Running | Physical Digital Input |  |  | Yes | 10 |
| Unit 2 Available | Physical Digital Input |  |  | Yes | 11 |
| Unit 2 Motor Overload | Physical Digital Input |  |  | Yes | 12 |
| Unit 2 Motor Over temperature | Physical Digital Input |  |  | Yes | 13 |
| Unit 2 Stator Leakage | Physical Digital Input |  |  | Yes/No | 14 |
| Unit 2 Starter Over temperature | Physical Digital Input |  |  | Yes/No | 15 |
|  | Physical Digital Input |  |  |  | 16 |
| EXPANSION MODULE 5414 |  |  |  |  |  |
| SCADA Inhibit Override | Physical Digital Input |  |  | Yes | 0 |
| Wet Well Not High | Physical Digital Input |  |  | yes | 1 |
| Wet Well No. 2 Not High | Physical Digital Input |  |  | Yes/No | 2 |
| Force Start Unit 1 | Physical Digital Input |  |  | Yes | 3 |
| Force Start Unit 2 | Physical Digital Input |  |  | Yes | 4 |
| Bypass Cut In Level | Physical Digital Input |  |  | Yes/No | 5 |
| Bypass Cut Out Level | Physical Digital Input |  |  | Yes/No | 6 |
|  | Physical Digital Input |  |  |  | 7 |
| Arc Fault Detection Healthy | Physical Digital Input |  |  | Future | 8 |
| Arc Fault Tripped | Physical Digital Input |  |  | Future | 9 |
| Automatic Transfer Switch Healthy | Physical Digital Input |  |  | Yes/No | 10 |
| Generator Fuel Level Not Low | Physical Digital Input |  |  | Yes/No | 11 |
| Generator Running | Physical Digital Input |  |  | Yes/No | 12 |
| Generator Fault | Physical Digital Input |  |  | Yes/No | 13 |
| Generator Service Required | Physical Digital Input |  |  | Yes/No | 14 |
|  | Physical Digital Input |  |  |  | 15 |
| BASE UNIT 575 |  |  |  |  |  |
| Unit 1 Start Request | Physical Digital Output |  |  |  | 1 |
| Unit 1 Motor Overload Reset | Physical Digital Output |  |  |  | 2 |
| Unit 1 Inhibited | Physical Digital Output |  |  |  | 3 |
|  | Physical Digital Output |  |  |  | 4 |
|  | Physical Digital Output |  |  |  | 5 |
| Command to Run on Battery | Physical Digital Output |  |  |  | 6 |
| Pump Station Called | Physical Digital Input |  |  |  | 7 |
| UWSS Telemetry Fail | Physical Digital Input |  |  |  | 8 |
| EXPANSION MODULE 6601 |  |  |  |  |  |
| Unit 2 Start Request | Physical Digital Output |  |  |  | 1 |
| Unit 2 Motor Overload Reset | Physical Digital Output |  |  |  | 2 |
| Unit 2 Inhibited | Physical Digital Output |  |  |  | 3 |
|  | Physical Digital Output |  |  |  | 4 |
| Master Fault | Physical Digital Output |  |  |  | 5 |
| Odour Control Solenoid Valve Open Request | Physical Digital Output |  |  |  | 6 |
| Generator Test Request | Physical Digital Output |  |  |  | 7 |
| Peer Telemetry Fail | Physical Digital Output |  |  |  | 8 |

| BASE UNIT 575 |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Wet Well Level | Physical 32 bit Analog Input |  | m | Yes | 1 |
| Delivery Pressure | Physical 32 bit Analog Input |  | m | Yes/No | 2 |
|  | Physical 32 bit Analog Input |  |  |  | 3 |
| Flow Rate See Note 5 | Physical 32 bit Analog Input |  | L/s | Yes/No | 4 |
| Unit 1 Power | Physical 32 bit Analog Input |  | kW | Yes/No | 5 |
| Unit 1 Current | Physical 32 bit Analog Input |  | A | Yes | 6 |
| EXPANSION MODULE 6601 |  |  |  |  |  |
| Wet Well Level 2 | Physical 32 bit Analog Input |  | m | Yes/No | 1 |
|  | Physical 32 bit Analog Input |  |  |  | 2 |
|  | Physical 32 bit Analog Input |  |  |  | 3 |
|  | Physical 32 bit Analog Input |  |  |  | 4 |
| Unit 2 Power | Physical 32 bit Analog Input |  | kW | Yes/No | 5 |
| Unit 2 Current | Physical 32 bit Analog Input |  | A | Yes | 6 |

Note 5	For WORM sites flow rate and flow total signals are from a 4-20mA signal.