Assets Delivery Group Infrastructure Design Branch

# Strategic Product Specification

# SPS 226

Dual Plate Non-Return Valves

version 1 revision 3

AUGUST 2016

# FOREWORD

Each Strategic Product Specification has been prepared to inform Water Corporation staff, consultants, contractors and land developers of the requirements for selecting and acquiring a manufactured product to be used in strategic Corporation infrastructure. The definition of ‘Product’ includes items that comprise assembled components, equipment or plant for mechanical, electrical and civil infrastructure applications.

The objective of a Strategic Product Specification is to specify fit-for-purpose Product which will contribute to the provision of effective water services at least whole-of-life cost and with least risk to service standards and safety. A Strategic Product Specification also provides uniform standards for compatibility of new water infrastructure with existing water assets.

Many Strategic Product Specifications have drawn on the design, asset management and operational experience of Product performance in live service gained by the Corporation over time.  Some Strategic Product Specifications have drawn on the experience of the water industry nationally by referencing Australian or WSAA standards.

Strategic Product Specifications are intended for reference and use in the following typical procurement scenarios:

- Capital funded infrastructure design and construction work;

- Private developer funded subdivision infrastructure for takeover by the Corporation;

- Operationally funded infrastructure design and construction work;

- Corporation period contracts for Product purchases;

- Product purchases for stock or for miscellaneous minor work.

A published Strategic Product Specification will, in some cases, comprise technical content that is typical of a range of products of the same type (type specification) but may exclude specific requirements that should apply to a particular project or application. In such cases, the project designer is required to document the supplementary project specific requirements in the appropriate Clause of the ‘Project Specific Requirements’ Appendix of the Specification.

The text of a published Specification should not be directly modified. In the event that a text variation is considered necessary to accommodate the needs of a particular project or application, the text modification should be documented in the appropriate Clause of a ‘Project Specific Requirements’ Appendix.

Deviation from the requirements of a Strategic Product Specification on a particular project is permissible only in special circumstances subject to consultation with The Principal Mechanical Engineer, Infrastructure Design Branch to whom all enquiries relating to the technical content of the Specification should be directed.

Your participation, as a user of the Specification, in its ongoing review is invited with the intent of improving its value to your work and to that of other users.  All formal requests and suggestions for its improvement should be forwarded to The Principal Mechanical Engineer, Infrastructure Design Branch, who will ensure that your contribution is appropriately scheduled for action by the responsible Standards Custodian.

Improvements to the Specification will be published and issued to registered users on an as needs basis.

# Manager, Infrastructure Design Branch

This document is prepared without the assumption of a duty of care by the Water Corporation.  The document is not intended to be nor should it be relied on as a substitute for professional engineering design expertise or any other professional advice.

It is the responsibility of the user to ensure they are using the current version of this document.

© Copyright – Water Corporation: This standard and software is copyright.  With the exception of use permitted by the Copyright Act 1968, no part may be reproduced without the written permission of the Water Corporation.

# REVISION STATUS

# The revision status of this specification is shown section by section below:

| REVISION STATUS |
| --- |
| SECT. | VER./REV. | DATE | PAGES REVISED | REVISION DESCRIPTION (Section, Clause, Sub-Clause) | RVWD. | APRV. |
| 1 | 1/1 | 31.07.05 | All | New version using SPS template | EJP | AAK |
| 1 | 1/2 | 31.08.05 | 8 | 1.2 Amended | EJP | AAK |
| 1 | 1/3 | 30.08.16 | 7,8,11,12 | 1.1, 1.3 and Table 1.1 amended | SE | MP |
| 2 | 1/1 | 31.07.05 | All | New version using SPS template | EJP | AAK |
| 2 | 1/2 | 31.08.05 | 14 | 2.1 Amended | EJP | AAK |
| 2 | 1/3 | 30.08.16 | 13 | Table 2.1 Materials Revised | SE | MP |
| 3 | 1/1 | 31.07.05 | All | New version using SPS template | EJP | AAK |
| 3 | 1/2 | 31.08.05 | 17 | 3.10 Amended | EJP | AAK |
| 3 | 1/3 | 30.08.16 | 15,16 | 3.2, 3.6,3.10 Generally Revised | SE | MP |
| 4 | 1/1 | 31.07.05 | All | New version using SPS template | EJP | AAK |
| 4 | 1/3 | 30.08.16 | 17 | 4.1 Revised | SE | MP |
| 5 | 1/1 | 31.07.05 | All | New version using SPS template | EJP | AAK |
| 5 | 1/3 | 30.08.16 | 18 | 5.5.3 Revised | SE | MP |
| 6 | 1/1 | 31.07.05 | All | New version using SPS template | EJP | AAK |
| 7 | 1/1 | 31.07.05 | All | New version using SPS template | EJP | AAK |
| 7 | 1/3 | 30.08.16 | 21 | 7.2 Revised | SE | MP |
| 8 | 1/1 | 31.07.05 | All | New version using SPS template | EJP | AAK |
| 9 | 1/1 | 31.07.05 | All | New version using SPS template | EJP | AAK |
| 10 | 1/1 | 31.07.05 | All | New version using SPS template | EJP | AAK |
| 11 | 1/1 | 31.07.05 | All | New version using SPS template | EJP | AAK |
| 11 | 1/3 | 30.08.16 | 26 | 11.2 Amended | SE | MP |
| 12 | 1/1 | 31.07.05 | All | New version using SPS template | EJP | AAK |
| 13 | 1/1 | 31.07.05 | All | New version using SPS template | EJP | AAK |
| 13 | 1/3 | 30.08.16 | 30,31 | App C Table Generally Revised | SE | MP |

# Strategic Product Specification

# SPS 226

Dual Plate Non-Return Valves

# CONTENTS

Section	Page

1	Scope and General	7

1.1	Scope	7

1.2	Referenced Documents	7

1.3	Definitions and Notation	8

1.3.1	Allowable operating Pressure	8

1.3.2	Allowable Test Pressure	8

1.3.3	Bulk Head Test	8

1.3.4	Certificate	9

1.3.5	Certification Body	9

1.3.6	Certification Mark	9

1.3.7	Certification Scheme	9

1.3.8	Coating	9

1.3.9	Coating Defect	9

1.3.10	Compliant Product	9

1.3.11	Corporation	9

1.3.12	Free End Test	9

1.3.13	Manufacturer	9

1.3.14	Maximum Allowable Operating Pressure	9

1.3.15	Nominal Size (DN)	10

1.3.16	Non-Return Valve	10

1.3.17	Notation	10

1.3.18	Officer	10

1.3.19	Pressure Class (PN)	10

1.3.20	Product	10

1.3.21	Product Appraisal	10

1.3.22	Product Assessor	10

1.3.23	Product Certification	10

1.3.24	Product Verification Report	11

1.3.25	Product Warranty	11

1.3.26	Purchasing Schedule	11

1.3.27	Quality System	11

1.3.28	Reverse Velocity	11

1.3.29	Strategic Product	11

1.3.30	Supplier	11

1.3.31	Testing	11

1.3.32	Valve	12

1.3.33	WSAA	12

1.4	Valve Type	12

1.5	Designation of Size	12

1.6	Allowable Operating Pressure and Required Test Pressures	12

2	Materials and Components	13

2.1	General	13

2.2	Dezincification-Resistant materials	13

2.3	Contamination of Water	13

2.4	Elastomeric Materials	13

2.5	Castings	14

2.6	Selection of Materials	14

3	Design	15

3.1	General	15

3.2	Performance	15

3.3	Body	15

3.4	Valve Seat	15

3.5	Plates	15

3.6	Plate Springs	16

3.7	Hinge Pin	16

3.8	Bearings	16

3.9	Stop Pin	16

3.10	End Connections	16

3.11	Lifting Point	16

4	Protective Coatings	17

4.1	General	17

4.2	Coating Design	17

5	Testing	18

5.1	General	18

5.2	Notification of Testing	18

5.3	Access to the Place of Manufacture	18

5.4	Place of Manufacture other than WA	18

5.5	Performance Test Requirements	18

5.5.1	General	18

5.5.2	Body Hydrostatic Test	18

5.5.3	Valve Seat Test (Hi Pressure)	18

5.5.4	Valve Sensitivity Test (Lo Pressure)	19

5.5.5	Coating Tests	19

5.6	Test Certificates	19

6	Marking and Packaging	20

6.1	Marking	20

6.1.1	Body Markings	20

6.2	Packaging	20

6.2.1	General	20

6.2.2	Identification Tag	20

6.2.3	Marking of Packaging	20

7	Manuals	21

7.1	Format and Language	21

7.2	Content	21

8	Spare Parts and Special Tools	22

8.1	Interchangeability	22

8.2	Availability	22

8.3	Special Tools	22

9	Transportation, Handling and Storage	23

9.1	General	23

9.2	Preservation of Product in Storage	23

10	Quality Assurance	24

10.1	Certification	24

10.1.1	Certification of Product	24

10.1.2	Quality System	24

10.1.3	Product Re-verification	24

10.2	Compliance and Acceptance	24

10.2.1	Means of Demonstrating Compliance	24

10.2.2	Acceptance Criteria	24

10.3	Non-compliant Product	25

10.3.1	General	25

10.3.2	Manufacturing Repairs (In-process)	25

10.3.3	Product Warranty	25

10.3.4	Product Repair	25

11	Appendix A: Project Specific Requirements (Normative)	26

11.1	General	26

11.2	Technical Requirements	26

12	Appendix B: Technical Compliance Schedules (Normative)	27

12.1	Compliance Schedules	27

13	Appendix C: Material Master Records (Informative)	30

# Scope and General

## Scope

This Specification sets out requirements for the manufacture, supply, handling and delivery of dual plate (also referred to as dual flap) non-return valves.  The Specification also details the means by which compliance with the Specification shall be demonstrated and the criteria for acceptance.

Dual plate non-return valves are generally suited to applications with moderate system deceleration characteristics, in the order of 0-5 m/s-2.  Rapid response valves (SPS 230) may be required for more surge prone applications or where the higher capital cost is justified by lower operating cost (lower headloss) considerations.

Pressure Classes PN 16, 21, 25 and 35 for size DN 50 to DN 600 inclusive are covered, with maximum temperature of the operating fluid not exceeding 40˚C.

This specification covers the following:

a)	Wafer, lugged or double flanged body construction.

b)	Water supply applications including drinking water, recycled water and treated effluent.

Dual Plate nor-return valves are not suited to fluids containing fibrous materials such as unscreened raw sewage.

## Referenced Documents

The following documents are referenced in this Specification:

# API

594		Check valves – Wafer, wafer-lug and double flanged type

AS

1565		Copper and copper alloys – Ingots and castings

1646		Elastomeric seals for waterworks purposes

# 1646.1	General requirements

1830		Grey cast iron

1831		Ductile cast iron

2317		Collared eyebolts

2345		Dezincification resistance of copper alloys

2550.1	Cranes, hoists and winches Safe use - General

# 2550.3	Cranes, hoists and winches Safe use – Bridge, gantry, portal (including container cranes), jib and monorail cranes

2550.5	Cranes, hoists and winches Safe use – Mobile cranes

2550.11	Cranes, hoists and winches Safe use – Vehicle-loading cranes

3894.1	Site testing of protective coatings - Non-conductive coatings - Continuity testing - High voltage ('brush') method

4087		Metallic flanges for waterworks purposes

4020		Products for use in contact with drinking Water Corporation

4158		Thermal-bonded polymeric coatings on valves and fittings for water industry purposes

EN

EN1092-1 Flanges and their joints - Circular flanges for pipes, valves, fittings and accessories, PN designated - Part 1: Steel flanges

EN1092-2 Circular flanges for pipes, valves, fittings and accessories, PN designated - Part 2: Cast iron flanges

# AS/NZS ISO

- Quality management systems – requirements

ISO/IEC

17025		General requirements for the competence of testing and calibration laboratories

# ASTM

A276		Standard Specification for Stainless Steel Bars and Shapes

A313M	Standard Specification for Stainless Steel Spring Wire

A351M	Standard Specification for Castings, Austenitic, Austenitic-ferritic (Duplex), for pressure containing parts

# SAA Guides

HB 18.2	Guide 2-General terms and their definitions concerning standardization and related activities

HB 18.22 	Guide 22-Information on manufacturer’s declaration of conformity with standards and other technical specifications

HB 18.23	Guide 23-Methods of indicating conformity with standards for third-party certification systems

HB 18.28	Guide 28-General rules for model third-party certification system for products

MP 52	Manual of authorization procedures for plumbing and drainage products

Corporation Technical Specifications

DS95 	Standard for the selection, preparation, application, inspection and testing of protective coatings on Water Corporations assets

A1	Surface Preparation for the application of protective coatings on Steel and/or Cast Iron

E2	Epoxy mastic coating on new & existing control valves

## Definitions and Notation

### Allowable operating Pressure

The allowable internal pressure, which the valve can safely withstand in service.

### Allowable Test Pressure

The maximum internal hydrostatic pressure, which the valve can withstand during testing.

### Bulk Head Test

A test where the testing machine provides external restraint, in order to make a watertight joint at each end of the valve.

### Certificate

A formal certificate defined in SAA HB 18.2 and operated in accordance with SAA HB 18.22 that, as an outcome of Product Certification, attests Product conformity with the nominated product and test standards and authorizes the use of a Certification Mark.

### Certification Body

An independent (or third party) organisation duly accredited by the Joint Accreditation System of Australia and New Zealand (JAS-ANZ) to operate Certification Schemes.

In the case of a non-strategic plumbing Product, a Certification Body means an organisation approved by Standards Australia to administer the National Certification of Plumbing and Drainage Products (NCPDP) Scheme in accordance with SAA MP 52.

### Certification Mark

A trademark or other mark of product conformity with a specified standard defined in SAA HB 18.2 and applied in accordance with SAA HB 18.23 that is issued under the rules of a Certification Scheme.

### Certification Scheme

A product certification program or system which is operated in accordance with JAS-ANZ Procedure 15 – General requirements for bodies operating product certification systems and in accordance with the general rules of SAA HB 18.28 and System No. 5 as defined in ISO/ITC publication - Certification - Principles and practice. In the case of a non-strategic plumbing Product, a Certification Scheme means the NCPDP Scheme.

NOTE:	The effect of this is to require maintenance by the manufacturer of effective production control planning in addition to full type testing from independently sampled production and subsequent verification of conformity with specified standards.

### Coating

A corrosion-inhibiting medium applied to the product surface.

### Coating Defect

A physical defect in the corrosion-inhibiting medium applied to the product surface.

### Compliant Product

Product that has been assessed, by means of Product Appraisal, as conforming with standards and specifications that are nominated by the Corporation.

### Corporation

The Water Corporation of Western Australia.

### Free End Test

A test where the valve’s ends are blanked off so that the axial hydraulic force is not externally restrained.

### Manufacturer

An entity or combination of entities that is responsible for selection, processing and control of Product constituent materials or compounds and for the processing equipment that collectively result in the manufactured product.

### Maximum Allowable Operating Pressure

The allowable internal pressure, including surge that a component can safely withstand in service.

### Nominal Size (DN)

An alphanumeric designation of size for components of a pipework system, which is used for reference purposes. It comprises the letters DN followed by a dimensionless whole number which is indirectly related to the physical size, in millimetres, of the bore or outside diameter of the end connections

### Non-Return Valve

A valve that prevents reversal of flow by automatic closure of a plate, flap or other mechanism.

### Notation

Statements expressed by use of the word ‘shall’ are mandatory or ‘normative’ requirements of the Specification. Statements expressed by use of the words ‘should’ or ‘may’ are ‘informative’ but not mandatory and are provided only for information and guidance. Notes in Specification text are informative. Notes that form part of Specification Tables are normative. An Appendix to the Specification that is designated ‘normative’ contains mandatory requirements. An Appendix that is designated ‘informative’ is provided for information and guidance only. The term ‘specified’ includes requirements of the Specification and requirements stated or referenced in other project documentation.

### Officer

A duly authorised representative or appointed agent of the Corporation.

### Pressure Class (PN)

A classification of pressure by PN number, based on the allowable operating pressure (AOP) expressed in Megapascals (PN = 10 x AOP).

### Product

A single unit or multiple units of manufactured end product or an assembly of manufactured component products, materials or equipment. This Specification and accompanying Purchasing Schedule define the nature and details of Product to be supplied.

NOTE 1:	An end product is most commonly an output of manufacturing processes that result in finished end products having the same features and characteristics and can be the result of a single or multiple production batches.

NOTE 2:	Manufactured equipment and assemblies of Product components or materials are commonly procured for mechanical, electrical and civil infrastructure applications.

### Product Appraisal

A formal process whereby Product, including product design, is subjected to systematic engineering assessment to determine Product fitness for prescribed end uses and to evaluate the extent of Product and production systems conformity with nominated standards and specifications. Product Appraisal includes verification of the extent of compliance in accordance with the requirements of a relevant ‘Technical Compliance Schedule’ Appendix.

### Product Assessor

An organization, Officer or other person who, having demonstrated specialist product knowledge and competence acceptable to the Corporation, is nominated by the Corporation, subjects Product to Product Appraisal and issues one or more Product Verification Reports.

### Product Certification

A formal process whereby the production and management systems for the manufacture of Product, are assessed by a Certification Body to evaluate compliance of these systems with prescribed product standards and tests, under Certification Scheme rules.

### Product Verification Report

A formal report wherein a Product Assessor evaluates the extent of Product compliance with the nominated product standards and specifications.

NOTE:	Verification may be on a project-by-project basis or at agreed intervals, as appropriate to the scope of a Purchasing Schedule and Product end use, subject to determination by the Corporation.

### Product Warranty

A formal express undertaking by a Supplier or Manufacturer that Product is:

•	In conformity with the nominated product specification and referenced standards;

•	Fit for the nominated Product end use or application;

•	Designed for sustained operation at the nominated service performance levels for the specified design life;

•	Adequately packaged for intended transportation, handling and storage conditions;

•	Supported by English language installation, operating and servicing instructions;

•	Adequately supported by Supplier capacity to provide technical Product support.

NOTE:	Where required, a Product Warranty should indemnify the Corporation against claims made or losses suffered as a result of breach of the Warranty by means of Public and Products Liability Insurances as specified in the undertaking.

### Purchasing Schedule

A Corporation purchase order, tender, schedule of prices, bill of quantities, or specification that details the nature, quantity and other characteristics of Product to be supplied, purchased or installed.

### Quality System

A management system that establishes, documents, implements and maintains organizational structures, resources, responsibilities, processes and procedures for the manufacture of Product and provision of Product related services in accordance with the requirements of AS/NZS ISO 9001.

### Reverse Velocity

The velocity of the reverse flow in the piping system, based on nominal pipe diameter, at the instant that the valve plates close against the seat.  The magnitude of the surge pressure resulting from valve closure is a function of reverse velocity which can be approximated from the Joukowsky equation.

### Strategic Product

An essential product whose performance is critical in eliminating risk to the safe and effective provision of water services, which are functions of the Corporation under the Water Corporation Act as licensed under the Water Services Coordination Act.

NOTE 1:	Strategic product is most commonly an element of permanent Corporation infrastructure. Ancillary operational and safety equipment, not intended to form part of this infrastructure, may be considered strategic by virtue of enhanced operational performance or personnel safety.

NOTE 2:	Plumbing products (end-of-line water service fittings DN 32 or smaller) used in strategic services may, by virtue of statutory and regulatory requirements, be considered strategic in Corporation applications.

### Supplier

An entity or combination of entities that is responsible for the supply of Product.

NOTE:	A Supplier may be a Product manufacturer, owner, producer, distributor or vendor or an agent, tenderer or contractor for supply of Product or Product related service.

### Testing

The determination of Product characteristics by inspection and by the application of specified test procedures.

### Valve

Valve or valves shall mean dual plate non-return valve or valves supplied in new unused condition.

### WSAA

The Water Services Association of Australia of which the Water Corporation is a corporate member.

## Valve Type

Valves shall be flangeless, lugged or a double flanged spool body type designed for use with the axis of the body and ports in either the horizontal or vertical up-flow position. The valve shall be suitable for above ground or below ground service and for use with water or recycled effluent.

NOTE:		Valves are not suitable for use in sewage or where solids or fibrous material may be present.

## Designation of Size

Valve size shall be designated by the nominal size as follows: DN 50, DN 80, DN 100, DN 150,

DN 200, DN 250, DN 300, DN 400, DN 500, and DN 600.

## Allowable Operating Pressure and Required Test Pressures

Allowable operating and required test pressures shall as shown in Table 1.1.

# TABLE 1.1 – ALLOWABLE OPERATING AND REQUIRED TEST PRESSURES

| Class of Valve | Allowable Operating Pressure, kPa | Seal Hi Test Pressure kPa | Seal Lo Test Pressure kPa | Body Test Pressure, kPa |
| --- | --- | --- | --- | --- |
| 16 | 1600 | 1760 | 100 | 2400 |
| 21 | 2100 | 2310 | 100 | 3150 |
| 25 | 2500 | 2750 | 100 | 3750 |
| 35 | 3500 | 3850 | 100 | 5250 |

# Materials and Components

## General

Materials and components shall comply with the requirements of Table 2.1. The materials listed are minimum acceptable standard materials. Other materials may be used, provided they are equivalent in performance, particularly with respect to strength, corrosion-resistance, valve operation and durability.

Non-metallic valve component materials shall be fit for purpose and shall exhibit dimensional stability after extended periods of time immersed in water.

Note: 		Not applicable to Seawater applications.

# TABLE 2.1 – MINIMUM MATERIAL REQUIREMENTS

| Valve Components | Materials | Standard and Grade |
| --- | --- | --- |
| Body <= DN300 | Stainless steel | ASTM A351M | CF-8M |
|  | Aluminium bronze | AS 1565 | C95810 |
| Body > DN300 (Refer Section 2.6) | Ductile cast iron1 | AS 1831 | 400-12, 500-7 |
|  | Aluminium bronze | AS 1565 | C95810 |
|  | Stainless steel | ASTM A351M | CF-8M |
| Plates | Aluminium bronze | AS 1565 | C95810 |
|  | Stainless steel | ASTM A351M | CF-8M |
| Hinge pin, stop pin | Stainless steel | ASTM A276 | 316 |
| Pin retainer2 | Stainless steel | ASTM A276M | 316 |
| Plate springs | Stainless steel | ASTM A313M | 316 |
| Snap ring | Stainless steel | ASTM A313M | 316 |
| Seat | NBR, EPDM, Viton | AS 1646 |  |
| Plate and body lug bearings | Glass-filled PTFE |  |  |
| Spring bearings | Virgin PTFE |  |  |
| Pin retainers2 | Stainless steel | ASTM A276 | 316 |
| Support sleeve2 | Stainless steel | ASTM A276 | 316 |

# NOTES

1.	Ductile cast iron materials shall be of retainer-less design and total coating encapsulation.

2.	Where applicable.

## Dezincification-Resistant materials

Copper alloy valve components shall be dezincification resistant and shall comply with AS 2345.

## Contamination of Water

Components in contact with drinking water shall comply with AS/NZS 4020.  International equivalent standards may be permitted, subject to approval.

## Elastomeric Materials

Elastomeric materials shall be made of material that is not injuriously affected by the fluid, temperature or environmental conditions to which the O-ring will be subjected in service.

## Castings

Castings shall be free from structural defects, laps, blowholes, pitting and sand inclusions. No repairs shall be permitted on structural defects.

## Selection of Materials

Where a range of materials are allowable (eg =>DN300), suppliers are requested to provide pricing for all material options available.

# Design

## General

Valves shall be designed to operate smoothly with both plates assuming a stable operational position over the velocity flow range specified in the purchasing schedule. On cessation of flow through the valve, both plates shall seat rapidly and simultaneously at the onset of reverse flow. The design criteria of the valve and fasteners should be based on a minimum life expectancy of 50 years.

## Performance

The valve shall be designed to operate:

- Within the range of maximum and minimum flows specified in the purchasing schedule

- At the maximum flow deceleration rate specified in the purchasing schedule.

- At the maximum and minimum operating pressures specified in the purchasing schedule.

## Body

Valves manufactured with hinge and stop pins that are secured by penetrating the valve body shall be manufactured from a corrosion resistant material. Ferrous bodied valves (e.g. cast iron and ductile iron) shall incorporate a separate pin retainer or insert for securing the hinge and stop pins in order to obviate body penetration into the body. Ferrous bodies shall be coated in accordance with Section 4.

## Valve Seat

The plates shall seal onto a resilient seat which shall be fusion bonded to the valve body.

## Plates

The valve shall incorporate two spring-loaded semi-circular plates hinged from a centrally mounted hinge pin. The plates shall fully open into the internal diameter of adjacent pipe without fouling for the valve sizes and pipe diameters shown in Table 3.1.

# TABLE 3.1 INTERNAL DIAMETER OF ADJACENT PIPE

| Nominal Size DN | Internal Diameter of Adjacent Pipe - mm |
| --- | --- |
| 100 | 86 |
| 150 | 140 |
| 200 | 191 |
| 250 | 245 |
| 300 | 290 |
| 400 | 376 |
| 4501 | 427 |
| 500 | 478 |
| 600 | 574 |

# NOTE:  1. Non preferred size

## Plate Springs

Valves ≥DN 150 shall have 2 or more independent springs to operate the plates.

The primary consideration in the selection of plate springs is the attainment of acceptable reverse velocity, VR, which shall be determined as follows:

- The transient pressure rise that is caused at valve closure added to the system pressure at the time of valve closure shall not exceed the allowable operating pressure of the valve.

- The reverse velocity, VR shall not exceed the following values:

| Operation | Environmentally sensitive locations | Remote locations |
| --- | --- | --- |
| Normal steady state operation | 0.15 m/s | 0.20 m/s |
| Less frequent operation (<10% of stop cycles) | 0.20 m/s | 0.25 m/s |
| Infrequent operation (≤ 1% of stop cycles) | 0.25 m/s | 0.30 m/s |

The secondary consideration is to ensure that the plates are fully open at minimum flow to prevent plate chatter inducing spindle wear or premature spring failure.

Note:	Spring selection is of increasing importance with size, pressure and system deceleration.  Hydraulic analysis should be undertaken to determine system characteristics for higher pressures and sizes =>DN300.

## Hinge Pin

The hinge pin shall be sized so that the bearing stress imposed by the hinge bearings produces minimal wear on either the pin or hinge bearings.

## Bearings

Valves shall be fitted with plate lug, body lug and spring bearings.  Valve sizes DN 600 and larger shall incorporate a support or other method in the hinge mechanism to prevent one plate bearing on the other.

NOTE:	For large diameter valves (e.g. ≥DN 600) installed in the vertical position, one plate resting on the other produces a high friction force in the lower body lug bearing and produces delayed closing of one plate with respect to the other.

## Stop Pin

A stop pin shall be provided downstream of the hinge to act as a stop for both plates when they are in their fully open position.

## End Connections

The valve end connections for sizes <DN 300 shall be of either the wafer flangeless or wafer lugged construction and for sizes =>DN300 shall be of double flanged construction, as nominated in the purchasing schedule.  Wafer flangeless valve bodies shall be sized to fit between assembled flange bolts for AS 4087 or EN1092 flanges as applicable.  Lugged and double flanged valve drilling shall comply with EN1092 (PN25 applications) or AS 4087 (all other applications).   Valve flanges shall be full faced and parallel.

Face-to-face dimensions shall comply with API 594.

## Lifting Point

Valves exceeding 25 kg shall be provided with a means for lifting. Collared eyebolts shall comply with AS 2317.

# Protective Coatings

## General

Bronze or stainless steel body valve bodies (<= DN300) shall be uncoated.

Ductile iron body valves (>DN300) shall have a thermally bonded polymeric coating to AS4158 (preferred), or a two coat high build epoxy coating in accordance with Corporation Technical Specifications A1 and E2  (only permitted where thermally bonded coating not available).

All other valve components shall be constructed from corrosion resistant materials.

## Coating Design

The corrosion protection system shall be fully effective for all internally wetted surfaces. The coating of ductile iron components at all dissimilar metal interfaces shall form a complete seal in order to prevent formation of galvanic couples. This includes seat-retaining screws, which shall be sealed via the coating or an effective thread sealant. All surfaces that cannot be effectively coated and tested shall be of corrosion-resistant materials.

# Testing

## General

Product shall be tested in accordance with the test requirements of this Specification. Testing shall be deemed acceptable when test outcomes have been formally verified by a Certification Body or witnessed by a testing Officer. Product for which a test requirement has not been met shall be classified as non-compliant Product.

NOTE 1:	Testing should be carried out by an organisation accredited by NATA or in accordance with ISO/IEC 17025.

NOTE 2:	A testing Officer should normally be an Officer who has specialist knowledge of or training in product or materials testing appropriate to the Product characteristics to be tested.

## Notification of Testing

The Corporation shall be notified in writing of each formal test proposal at least seven (7) days prior to the preparation of Product for testing except where a specified test has been the subject of a current valid Certificate issued by a Certification Body. This notification is required to enable the Corporation to make all necessary arrangements including appointment of a testing Officer in a timely manner.

## Access to the Place of Manufacture

The testing Officer shall be afforded access, at all reasonable times, to all places of manufacture of Product or product components and shall be authorised to arrange or undertake such testing there as the Corporation deems appropriate to the testing regime specified.

## Place of Manufacture other than WA

Where any Product or product component is being manufactured other than in Western Australia the Corporation may appoint a local inspecting Officer to undertake inspections and witnessed testing as required. The testing Officer shall be provided with all due authority and permits required to carry out testing at the place of manufacture.

NOTE 1:	The cost of witnessed testing arranged by the Corporation will normally be borne by the Corporation unless otherwise negotiated.

## Performance Test Requirements

### General

Each valve shall be hydrostatically tested with water in accordance with Clauses 5.5.2, and 5.5.3. Valves of nominal sizes up to and including DN 300 may use a bulkhead test. Valves of nominal sizes larger than DN 300 shall be subject to a free end test. Leakage at pressure-containing joints shall not be a cause for failure of the test. Valve coatings shall be tested in accordance with Clause 5.5.4.

### Body Hydrostatic Test

For valve sizes ≤ DN 300 with the plates in the open position, the body shall be hydrostatically tested for 1 minute at the allowable test pressure for the particular class of valve shown in Table 1.1.  Valves greater than DN 300 shall be tested as above for a minimum of 2 minutes.  There shall be no leakage through the body nor shall any part be permanently deformed.

### Valve Seat Test (Hi Pressure)

For valve sizes ≤ DN 300 the seat seal shall be hydrostatically tested for 1 minute at a pressure equal to 1.1 times the allowable operating pressure for the particular class of valve shown in Table 1.1.  Valves greater than DN 300 shall be tested at the same pressure as above for a minimum of 2 minutes. The pressure shall be applied hydrostatically to the outlet side of the valve with the inlet side of the valve open to the atmosphere.  There shall be no leakage past the seat or through the body i.e. valve shall be drop-tight.

### Valve Sensitivity Test (Lo Pressure)

Following the valve seat test an additional seat test shall be conducted in the same manner at a pressure of 100 kPa. There shall be no leakage past the seat.

### Coating Tests

Polymeric coated valves shall be tested in accordance AS/NZS 4158.

The entire coated surface (except for external corners or embossed areas) shall be tested for coating continuity using a fully variable DC high voltage holiday detector in accordance with AS 3894.1.  Defects found during testing may be repaired, where allowable, in accordance with AS/NZS 4158.  Where a coating defect cannot be repaired, the valve shall be rejected.

## Test Certificates

For the purposes of acceptance, each test certificate shall, as a minimum, bear the relevant Product item serial number and shall certify that the Product item has complied with the specified test requirements.

# Marking and Packaging

## Marking

### Body Markings

Each Product shall have the following information clearly marked by casting on the body, or displayed by stamping or engraving on a corrosion resistant plate which shall be permanently secured using corrosion resistant fasteners:

# (a)	Manufacturer’s name or trademark.

# (b)	Nominal diameter (DN)

# (c)	Year of manufacture.

# (d)	Valve Pressure Class

# (e)	Serial number

# (f)	Direction of flow.

Cast lettering shall be as large as practicable.

## Packaging

### General

Product shall be packaged with appropriate protection, which shall prevent damage or defects as a result of handling, storage or transportation. Flexible packaging material shall have a minimum expected life in outside storage conditions of 12 months from the date of delivery.

### Identification Tag

Wherever requested in the Purchasing Schedule each Product item shall be identified using a weatherproof marking pen on a corrosion resistant metal identification tag securely wired to the Product in a conspicuous position using a galvanized tie wire with the following information:

a)	Material Master Record number

- Contract number

- Purchase order number.

### Marking of Packaging

Where requested in the purchasing schedule, the Product shall be identified by marking on the outside of any protective packaging the same information as shown on the identification tag.

# Manuals

## Format and Language

Where required, Product shall be supplied complete with appropriate installation, operation and maintenance instructions or manuals, in clear diagrammatic and text format, in English

## Content

The manuals shall contain all the relevant information required to commission and maintain the Product in operational service, including the following:

a)	Product technical data sheet identifying all selected options

b)	Installation and commissioning instructions

c)	Maintenance and Troubleshooting guidelines

d)	Test Certificates

e)		Complete list of parts and associated exploded views or sectional diagrams and reference part numbers

# Spare Parts and Special Tools

## Interchangeability

All spare parts shall be interchangeable for a manufacturer’s product of the same size and model.

## Availability

Spare parts and servicing facilities for the product shall be readily available in Western Australia.

## Special Tools

Any special tools required for service and maintenance of the product shall be supplied.

# Transportation, Handling and Storage

## General

Transportation, handling and storage facilities shall be designed to prevent Product damage or defects and to maintain Product free of deleterious matter. Product shall not be dropped off elevated vehicle platforms or sites. Mechanical handling equipment shall be in accordance with AS 2550.1, AS 2550.3, AS 2550.5 and AS 2550.11 and shall be appropriate to the loads to be lifted. Manual handling shall be in accordance with the National Standard for Manual Handling and the National Code of Practice for Manual Handling, published by National Occupational Health and Safety Commission, Australia. Product restraint during transportation shall be in accordance with Load Restraint Guide—Guidelines for Safe Carriage of Loads on Road Vehicles, published jointly by the Federal Office of Road Safety and the National Road Transport Commission, Australia.

NOTE:	Where wire ropes or chains are used, these should not come into direct contact with Product. Lifting elements in direct contact with Product should be of a non-abrasive design e.g. elastomeric or fabric webbing straps. During transportation, Product restraints should be checked for tension at regular intervals of travel and should not be released until the transporting vehicle is resting in a secure stable disposition on level ground.

## Preservation of Product in Storage

Product shall be stored in original Product packaging in accordance with the published requirements of the manufacturer, prior to installation. Sensitive component materials shall be protected from extended exposure to direct sunlight and high temperatures e.g. elastomeric components shall be stored in accordance with the general principles of AS 1646.1 Clause 6. Designated Product storage areas shall be of sufficient size to accommodate Product deliveries and shall be flat, reasonably level and free of combustible vegetation, sharp stones or projections that could cause Product damage or defects.

# Quality Assurance

## Certification

### Certification of Product

Wherever this Specification requires compliance with nominated Product and test Standards, conformance shall be certified by means of a Certification Scheme, conducted by a Certification Body. Each Certificate shall expressly attest compliance of all Product items with the nominated Standards. Wherever specified, Certificates shall be submitted to the Officer nominated for this purpose. Product shall be marked in accordance with the requirements of the Certification Body.

NOTE:	Compliance of Product including related accessories and services with nominated Standards and specified requirements may be verified by means of a Product Verification Report provided by a Product Assessor. The Product Verification Report should identify all relevant Certificates of Product compliance, duly issued in accordance with Certification Scheme rules.

### Quality System

The processes for manufacture, testing, supply, transportation, handling, delivery and storage of Product to be supplied in accordance with this Specification shall form part of a documented Quality System. The System shall be certified by a Certification Body as complying with the requirements of AS/NZS ISO 9001 and shall provide for identification and traceability, control of production and delivery to the specified destination, customer verification and control of documents and records.

### Product Re-verification

Product compliance with the Specification shall be subject to re-verification by a Product Assessor when, during the agreed Product supply period, there occurs any:

•	substantive change in Product design, material formulation or performance

•	Product failure to perform in operational service to the nominated performance specification.

Re-verification shall require the issue of a new or supplementary Product Verification Report. Product components and test outcomes that are not significantly affected by the Product change or failure may be excluded from the scope of re-verification, provided that these outcomes have already been reported in a current valid Product Verification Report that is acceptable to the Corporation.

Wherever the requirements of the Specification apply to a Product supply period in excess of three years, continuing acceptance of Product shall be subject to re-verification. The purpose of re-verification shall be to confirm the continuing compliance of Product quality and production control processes with the requirements of the Specification

## Compliance and Acceptance

### Means of Demonstrating Compliance

Compliance with this Specification shall be demonstrated by means of Product Appraisal and issue by a Product Assessor of a Product Verification Report that confirms compliance. Otherwise, Product shall be deemed non-compliant and ineligible for registration as Product authorized for use in Corporation infrastructure.

NOTE 1:	Where a project includes design work including Product design, Product Appraisal may form part of the project design review process and the Product Assessor may be a member of the project design review team.

NOTE 2:	A Product Verification Report should verify the extent of compliance with the Specification including all relevant ‘Technical Compliance Schedule’ Appendices and the currency of a Certificate where relevant to the Product.

### Acceptance Criteria

For acceptance, Product shall be supplied as specified in the Purchasing Schedule.

Prior to the implementation of any arrangement to supply Product, the Supplier shall, in accordance with specified requirements:

•	nominate applicable Product Warranty terms; and

•	provide documentary verification in the form of a current valid Certificate or Product Verification Report as appropriate to the Product; and

•	detail each element of Product that does not comply with the specified requirements together with the extent of non-compliance.

NOTE:	Where the Specification includes Technical Compliance Schedules, the nature and extent of all non-compliances should be provided in accordance with the appropriate Schedules.

## Non-compliant Product

### General

Product whose design, workmanship or performance fails to conform to the specified requirements shall be clearly tagged and quarantined by the Supplier as non-compliant and shall be subject to rejection for return to and replacement by the Supplier.

Where the Specification includes a ‘Technical Compliance Schedule’, Product shall be deemed non-compliant except where a Supplier has demonstrated compliance in accordance with the requirements of the ‘Technical Compliance Schedule’ Appendices of the Specification.

### Manufacturing Repairs (In-process)

Welding, the use of fillers and other repairs shall generally not be permissible on Product which is in the course of production. Repairs to custom-built Products such as axially-split pumps and large valves may be considered only if determined by the Corporation to be minor casting repair work in non-strategic locations. Accordingly, details of any defect which the Manufacturer considers can be repaired; together with details of proposed repair procedures shall be submitted in writing for determination by the Corporation.

The Manufacturer shall make provision in its production Quality System and in the appropriate ITP’s for sufficient hold points whenever casting defects are encountered. Production work on non-compliant components shall cease and repair work shall not commence until the following details have been confirmed by the Corporation in writing that:

(a)	repair of the non-compliant components in lieu of their replacement is acceptable; and

(b)	proposed repair procedures are acceptable; and

(c)	any proposal to vary the terms of the original Product Warranty as a consequence of the in-process repair is acceptable.

### Product Warranty

The Supplier shall replace non-compliant Product with Product that conforms to the acceptance criteria or shall repair or rectify all faults, damage or losses caused by defective Product. Except as may otherwise be specified, the Product Warranty shall indemnify and keep indemnified the Corporation against all losses suffered by the Corporation as a result of non-compliant Product for a period no less than 24 months after Product delivery or 12 months after Product installation, whichever period elapses first.

### Product Repair

All reasonable proposals for repair or remedy of defects will be considered, provided that each such proposal is accompanied by a methodology statement that accords with the performance objectives of this Specification, as determined by the Corporation. For acceptance, a proposal for repair or remedy of Product defects shall not void or otherwise diminish the provisions of the Product Warranty.

# Appendix A: Project Specific Requirements (Normative)

## General

Project specific information and requirements, not included elsewhere in this Strategic Product Specification, shall apply as specified in the following Clauses.

## Technical Requirements

Table 11.1 details project specific requirements for the valves to be procured.

# TABLE 11.1: SCHEDULE OF PROJECT TECHNICAL REQUIREMENTS

| MMR No (where applicable) | No Off | DN | PN | Flow Range – max/min m/s | Pressure Range – max/min m water | System Deceleration m/s/s | Connection Type - Wafer / lugged /flanged | Connection Standard AS4087 / EN1092 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | / | / |  |  |  |
|  |  |  |  | / | / |  |  |  |
|  |  |  |  | / | / |  |  |  |
|  |  |  |  | / | / |  |  |  |
|  |  |  |  | / | / |  |  |  |
|  |  |  |  | / | / |  |  |  |

# Appendix B: Technical Compliance Schedules (Normative)

## Compliance Schedules

Suppliers shall demonstrate Product compliance with the Specification by completing Technical Compliance Schedule 1 as shown in TABLE 12.1 on an item by item basis. For acceptance, the extent of scheduled technical item compliance shall be supported by verifiable documentary evidence. Each scheduled item nominates a Specification clause number with which the extent of Product compliance shall be demonstrated.

The Supplier shall denote compliance of an item by ticking the unshaded ‘Yes’ column appropriate to that item.  Where Product does not comply with specified requirements, the Supplier shall tick the ‘No’ column and shall detail the reasons for non-conformance and any proposed alternatives in the ‘Comments’ column. The Supplier shall denote acceptance and understanding of a Specification clause by ticking the corresponding ‘Noted’ column wherever unshaded.

Failure to notify the Corporation of all non-compliant Product components, including the extent of non-compliance, may void an accepted offer to supply or may result in rectification of all non compliant Product elements, at the Supplier’s cost.

# TABLE 12.1: TECHNICAL COMPLIANCE SCHEDULE 1

| Dual Plate Non-Return Valves |
| --- |
| Section/Clause | Noted | Compliance | Comments |
|  |  | Yes | No |  |
| 1. SCOPE AND GENERAL |
| 1.1 | Scope |  |  |  |  |
| 1.2 | Referenced Documents |  |  |  |  |
| 1.3 | Definitions and Notations |  |  |  |  |
| 1.4 | Valve Type |  |  |  |  |
| 1.5 | Designation of Size |  |  |  |  |
| 1.6 | Allowable Pressure |  |  |  |  |
| 2. MATERIALS AND COMPONENTS |
| 2.1 | General |  |  |  |  |
| 2.2 | Dezincification-Resistant Materials |  |  |  |  |
| 2.3 | Contamination of Water |  |  |  |  |
| 2.4 | Elastomeric Materials |  |  |  |  |
| 2.5 | Castings |  |  |  |  |
| 3. DESIGN |
| 3.1 | General |  |  |  |  |
| 3.2 | Performance |  |  |  |  |
| 3.3 | Body |  |  |  |  |
| 3.4 | Valve Seat |  |  |  |  |
| 3.5 | Plates |  |  |  |  |
| 3.6 | Plate springs |  |  |  |  |
| 3.7 | Hinge Pin |  |  |  |  |
| 3.8 | Bearings |  |  |  |  |
| 3.9 | Stop Pin |  |  |  |  |
| 3.10 | End Connections |  |  |  |  |
| 3.11 | Lifting Point |  |  |  |  |
| 4. COATINGS |
| 4.1 | General |  |  |  |  |
| 4.2 | Coating Design |  |  |  |  |
| 5. TESTING |
| 5.1 | General |  |  |  |  |
| 5.2 | Notification of Testing |  |  |  |  |
| 5.3 | Access to the Place of Manufacture |  |  |  |  |
| 5.4 | Place of Manufacture other than WA |  |  |  |  |
| 5.5 | Performance Test Requirements |  |  |  |  |
| 5.5.1 | General |  |  |  |  |
| 5.5.2 | Body Hydrostatic Tests |  |  |  |  |
| 5.5.3 | Valve Seat Test (Hi Pressure) |  |  |  |  |
| 5.5.4 | Valve Sensitivity Test (Lo Pressure) |  |  |  |  |
| 5.5.5 | Coating Tests |  |  |  |  |
| 5.6 | Test Certificates |  |  |  |  |
| 6. MARKINGS AND PACKAGING |
| 6.1 | Markings |  |  |  |  |
| 6.1.1 | Body Markings |  |  |  |  |
| 6.2 | Packaging |  |  |  |  |
| 6.2.1 | General |  |  |  |  |
| 6.2.2 | Identification Tag |  |  |  |  |
| 6.2.3 | Marking of Packaging |  |  |  |  |
| 7. MANUALS |
| 7.1 | Format and Language |  |  |  |  |
| 7.2 | Content |  |  |  |  |
| 8. SPARE PARTS & SPECIAL TOOLS |
| 8.1 | Interchangeability |  |  |  |  |
| 8.2 | Availability |  |  |  |  |
| 8.3 | Special Tools |  |  |  |  |
| 9. TRANSPORTATION, HANDLING AND STORAGE |
| 9.1 | General |  |  |  |  |
| 9.2 | Preservation of Product in Storage |  |  |  |  |
| 10. QUALITY ASSURANCE |
| 10.1 | Certification |  |  |  |  |
| 10.1.1 | Certification of Product |  |  |  |  |
| 10.1.2 | Quality System |  |  |  |  |
| 10.1.3 | Product Re-verification |  |  |  |  |
| 10.2 | Compliance and Acceptance |  |  |  |  |
| 10.2.1 | Means of Demonstrating Compliance |  |  |  |  |
| 10.2.2 | Acceptance Criteria |  |  |  |  |
| 10.3 | Non-compliant Product |  |  |  |  |
| 10.3.1 | General |  |  |  |  |
| 10.3.2 | Manufacturing Repairs |  |  |  |  |
| 10.3.3 | Product Warranty |  |  |  |  |
| 10.3.4 | Product Repair |  |  |  |  |

| Name of Supplier: |
| --- |
| Signature: | Date: |

When requested by the Corporation, the Supplier shall provide the information required by Technical Compliance Schedule 2 as shown in TABLE 12.2.

# TABLE 12.2: TECHNICAL COMPLIANCE SCHEDULE 2

| Dual Plate Non-Return Valves |
| --- |
| 1. SUPPLIER’S REPRESENTATIVE |  |
| 1.1 Full name |  |
| 1.2 Postal address |  |
| 1.3 Facsimile number |  |
| 1.4 Phone number |  |
| 2. QUALITY ASSURANCE |  |
| 2.1 Extent of third party accreditation of supplier |  |
| 2.2 Extent of third party accreditation of manufacturer |  |
| 2.3 Details of certificates and verification reports attached | (Yes/No) |
| 3. TECHNICAL INFORMATION |  |
| 3.1 Performance information e.g. head loss versus flow curves | (Yes/No) |
| 3.2 Details of the manufacturer’s inspection and testing plans supplied. | (Yes/No) |
| 3.3 Details of servicing facilities in Perth supplied. | (Yes/No) |
| 3.4 Additional pamphlets and drawings in conjunction with the technical literature supplied. | (Yes/No) |
| 4. PERFORMANCE GUARANTEES |  |
| 4.1 Manufacturer’s name |  |
| 4.2 Place of manufacture |  |
| 4.3 Model |  |
| 4.4 Type – flangeless, lugged or flanged |  |
| 4.5 Nominal size (DN) mm |  |
| 4.6 Pressure class (PN) kPa |  |
| 4.7 Deceleration m/s2 |  |
| 4.8 Maximum reverse velocity m/s |  |
| 4.9 Valve closure time sec |  |
| 5.0 MATERIALS) |  |
| 5.1 Body |  |
| 5.2 Plates |  |
| 5.3 Hinge pin, stop pin |  |
| 5.4 Pin retainer |  |
| 5.5 Plate springs |  |
| 5.6 Snap ring |  |
| 5.7 Seat |  |
| 5.8 Plate and body lug bearings |  |
| 5.9 Spring bearings |  |
| 5.10 Pin retainers screws |  |
| 6.0 DESIGN |  |
| 6.1 Flow velocity range for smooth stable operation m/s |  |
| 6.2 Maximum normal flow velocity m/s |  |
| 6.3 Maximum intermittent flow velocity m/s |  |
| 6.4 Flow Velocity to fully open valve m/s |  |
| 6.5 Cracking pressure for valve in the horizontal position kPa |  |
| 6.6 Method of securing resilient seat |  |
| 6.5 Upper plate support details for valves ≥DN 600 |  |
| 6.6 Wafer style end connection flange standard and face type |  |
| 6.7 Number of plate springs |  |
| 6.8 Flanged end connection flange standard |  |
| 6.9 Mass of valve kg |  |

| Name of Supplier: |
| --- |
| Signature: | Date: |

# Appendix C: Material Master Records (Informative)

The following Material Master Records (MMR) comprise Corporation catalogue numbers that are unique to the particular products described for the purposes of Corporation activities or work.

| MMR | PURCHASE ORDER LONG TEXT (Wafer Type - Stainless Steel - PN16) |
| --- | --- |
| 21654 | Valve, Check; Dual Flap; Flangeless Wafer Type; 316 Stainless Steel Body; DN50; PN16; Buna-N Seal; Serrated Face End Connections; To Suit AS 4087 Flanges |
| 21655 | Valve, Check; Dual Flap; Flangeless Wafer Type; 316 Stainless Steel Body; DN80; PN16; Buna-N Seal; Serrated Face End Connections; To Suit AS 4087 Flanges |
| 21656 | Valve, Check; Dual Flap; Flangeless Wafer Type; 316 Stainless Steel Body; DN100; PN16; Buna-N Seal; Serrated Face End Connections; To Suit AS 4087 Flanges |
| 21657 | Valve, Check; Dual Flap; Flangeless Wafer Type; 316 Stainless Steel Body; DN150; PN16; Buna-N Seal; Serrated Face End Connections; To Suit AS 4087 Flanges; Materials in Accordance with SPS226. Note: Specify Flow Range, Pressure Range and system deceleration (to ensure correct spring selection) when Ordering. |
| 21658 | Valve, Check; Dual Flap; Flangeless Wafer Type; 316 Stainless Steel Body; DN200; PN16; Buna-N Seal; Serrated Face End Connections; To Suit AS 4087 Flanges; Materials in Accordance with SPS226. Note: Specify Flow Range, Pressure Range and system deceleration (to ensure correct spring selection) when Ordering. |
| 21659 | Valve, Check; Dual Flap; Flangeless Wafer Type; 316 Stainless Steel Body; DN250; PN16; Buna-N Seal; Serrated Face End Connections; To Suit AS 4087 Flanges; Materials in Accordance with SPS226. Note: Specify Flow Range, Pressure Range and system deceleration (to ensure correct spring selection) when Ordering. |
| 21660 | Valve, Check; Dual Flap; Flangeless Wafer Type; 316 Stainless Steel Body; DN300; PN16; Buna-N Seal; Serrated Face End Connections; To Suit AS 4087 Flanges; Materials in Accordance with SPS226. Note: Specify Flow Range, Pressure Range and system deceleration (to ensure correct spring selection) when Ordering. |

| MMR | PURCHASE ORDER LONG TEXT (Wafer Lug Design - Stainless Steel - PN16) |
| --- | --- |
| 21661 | Valve, Check; Dual Flap; Wafer LugType; 316 Stainless Steel Body; DN50; PN16; Buna-N Seal; Serrated Face End Connections; Lug Design with Through-Bolt Holes to Protect Studs; To Suit AS 4087 Flanges |
| 21662 | Valve, Check; Dual Flap; Wafer Lug Type; 316 Stainless Steel Body; DN80; PN16; Buna-N Seal; Serrated Face End Connections; Lug Design with Through-Bolt Holes to Protect Studs; To Suit AS 4087 Flanges |
| 21663 | Valve, Check; Dual Flap; Wafer Lug Type; 316 Stainless Steel Body; DN100; PN16; Buna-N Seal; Serrated Face End Connections; Lug Design with Through-Bolt Holes to Protect Studs; To Suit AS 4087 Flanges |
| 21664 | Valve, Check; Dual Flap; Wafer Lug Type; 316 Stainless Steel Body; DN150; PN16; Buna-N Seal; Serrated Face End Connections; Lug Design with Through-Bolt Holes to Protect Studs; To Suit AS 4087 Flanges; Materials in Accordance with SPS226. Note: Specify Flow Range, Pressure Range and System Deceleration (To Ensure Correct spring Selection) when Ordering. |
| 21665 | Valve, Check; Dual Flap; Wafer Lug Type; 316 Stainless Steel Body; DN200; PN16; Buna-N Seal; Serrated Face End Connections; Lug Design with Through-Bolt Holes to Protect Studs; To Suit AS 4087 Flanges; Materials in Accordance with SPS226. Note: Specify Flow Range, Pressure Range and System Deceleration (To Ensure Correct Spring Selection) when Ordering. |
| 21666 | Valve, Check; Dual Flap; Wafer Lug Type; 316 Stainless Steel Body; DN250; PN16; Buna-N Seal; Serrated Face End Connections; Lug Design with Through-Bolt Holes to Protect Studs; To Suit AS 4087 Flanges; Materials in Accordance with SPS226. Note: Specify Flow Range, Pressure Range and System Deceleration (To Ensure Correct Spring Selection) when Ordering. |
| 21667 | Valve, Check; Dual Flap; Wafer Lug Type; 316 Stainless Steel Body; Dn300; PN16; Buna-N Seal; Serrated Face End Connections; Lug Design with Through-Bolt Holes to Protect Studs; To Suit AS 4087 Flanges; Materials in Accordance with SPS226. Note: Specify Flow Range, Pressure Range and System Deceleration (To Ensure Correct Spring Selection) when Ordering. |

| MMR | PURCHASE ORDER LONG TEXT (Double Flanged - Stainless Steel - PN16) |
| --- | --- |
| 21668 | Valve, Check; Dual Flap; Double Flange Type; 316 Stainless Steel Body; DN200; PN16; Buna-N Seal; Serrated Face End Connections; To Suit AS 4087 Flanges; Materials in Accordance with SPS226. Note: Specify Flow Range, Pressure Range and System Deceleration (To Ensure Correct Spring Selection) when Ordering. |
| 21669 | Valve, Check; Dual Flap; Double Flange Type; 316 Stainless Steel Body; DN250; PN16; Buna-N Seal; Serrated Face End Connections; To Suit AS 4087 Flanges; Materials in Accordance with SPS226. Note: Specify Flow Range, Pressure Range and System Deceleration (To Ensure Correct Spring Selection) when Ordering. |
| 21670 | Valve, Check; Dual Flap; Double Flange Type; 316 Stainless Steel Body; DN300; PN16; Buna-n Seal; Serrated Face End Connections; To Suit AS 4087 Flanges; Materials in Accordance with SPS226. Note: Specify Flow Range, Pressure Range and System Deceleration (To Ensure Correct Spring Selection) when Ordering. |

Note.  For higher pressures or larger sizes, the full specification together with Appendix A should be used.

# END OF DOCUMENT