## Design Sheet
UHF Radio Design
First Road to Second Road
Project Information | [7 empty] | Path Details | [5 empty] | Insert Alliance Partner Logo Here
| Project Name: | "Name" Water / Wastewater Scheme |  |  | Client: | 1 |  |  | Path Length (km) |  | 4.68
| Project No. | C - W0123456 |  |  | Project Manager: | Mr Pink
| Document No. |  |  |  | Design Manager: | Mr White |  | Design Requirements
[9 empty] | Fade Margin (dB) |  | 30
Site A Details |  |  |  | Site B Details |  |  |  |  | Radio Licence Type |  | PMP
| Name: | First Road |  |  | Name: | Second Road
| Latitude (GDA94) | -31 20 05.00 |  |  | Latitude (GDA94) | -31 17 33.69
| Longitude (GDA94) | 115 53 52.00 |  |  | Longitude (GDA94) | 115 54 09.21
| Easting (MGA 94) |  |  |  | Easting (MGA 94) |  |  |  | Measurements and Expected:
| Northing (MGA 94) |  |  |  | Northing (MGA 94) |  |  |  | Site A Antenna Height (AGL) | Site B Antenna Height (AGL) | RSSI First Road |  |  | RSSI Second Road
| Zone (MGA 94) |  |  |  | Zone (MGA 94) | [5 empty] | Measured (dBm) | DCF (dB) | Expected (dBm) | Measured (dBm) | DCF (dB) | Expected (dBm)
| RL (m) |  |  |  | RL (m)
| Bearing to Site B | 6 |  |  | Bearing to Site A | 186
Propagation Test Details: First Road |  |  |  | Propagation Test Details: Second Road
| TX Freq (MHz) | 461.325 | Calculated Gain/Loss |  | TX Freq (MHz) | 451.825 | Calculated Gain/Loss
| Radio Type | 64QAM - Low gain (50) |  |  | Radio Type | 64QAM - Low gain (50)
| Feeder Type | CNT-400 |  |  | Feeder Type | CNT-400
| Feeder Length (m) | 25 | -2.5 |  | Feeder Length (m) | 30 | -3
| Antenna Type (gain in dBi) | Unity Gain | 2 |  | Antenna Type (gain in dBi) | YBSS9 | 13 |  | 20 | 24 | -71 | 7.3 | -63.7 | -72 | 8.3 | -63.7
| Radio Cable Tail | Yes | -0.5 |  | Radio Cable Tail | Yes | -0.5 |  | 20 | 20 | -72 | 7.5 | -64.5 | -74 | 8.5 | -65.5
| Duplexer | Yes | -1.6 |  | Duplexer | No | 0 |  | 20 | 18 | -75 | 7.6 | -67.4 | -76 | 8.6 | -67.4
| Number of Connectors | 2 | -0.2 |  | Number of Connectors | 2 | -0.2 |  | 20 | 15 | -81 | 7.75 | -73.25 | -79 | 8.75 | -70.25
| Surge Arrester | No | 0 |  | Surge Arrester | No | 0 |  | 20 | 12 | -84 | 7.9 | -76.1 | -85 | 8.9 | -76.1
| Radio Power Output (dBm) | 32 | 32 |  | Radio Power Output (dBm) | 32 | 32 |  | 20 | 10 | -86 | 8 | -78 | -87 | 9 | -78
[9 empty] | 20 | 8 | -90 | 8.1 | -81.9 | -91 | 9.1 | -81.9
| Other Test Losses/Gains (loss -ve) | Misc | 0 |  | Other Test Losses/Gains (loss -ve) | Misc | 0 |  | 20 | 6 | -92 | 8.2 | -83.8 | -93 | 9.2 | -83.8
[9 empty] | 20 | 3 | -98 | 8.35 | -89.65 | -99 | 9.35 | -89.65
Proposed System: First Road |  |  |  | Proposed System: Second Road |  |  |  |  | 20 | 2 | -103 | 8.4 | -94.6 | -104 | 9.4 | -94.6
| Radio Type | 64QAM - Low gain (50) | Rec.Sensitivity (dBm) |  | Radio Type | 64QAM - Low gain (50) | Rec.Sensitivity (dBm)
|  |  | -94 |  |  |  | -94
| TX Freq (MHz) | 461 | Calculated Gain/Loss |  | TX Freq (MHz) | 451 | Calculated Gain/Loss
| Feeder Type | LDF4-50 |  |  | Feeder Type | LDF4-50
| Horizontal Feeder Length (m) | 10 |  |  | Horizontal Feeder Length (m) | 10
| Total Feeder Length (m) | 30 | -1.5 |  | Total Feeder Length (m) | 20 | -1
| Antenna Type (gain in dBi) | BA80 Dipole Array | 8 |  | Antenna Type (gain in dBi) | YBSS9 | 13
| Radio Cable Tail | Yes | -0.5 |  | Radio Cable Tail | Yes | -0.5
| Duplexer | Yes | -2 |  | Duplexer | No | 0
| Number of Connectors | 4 | -0.4 |  | Number of Connectors | 4 | -0.4
| Surge Arrester | Yes | -0.1 |  | Surge Arrester | Yes | -0.1
| Radio Power Output (dBm) | 33 | 33 |  | Radio Power Output (dBm) | 32 | 32
| Other Losses/Gains (loss-ve) | Misc | 0 |  | Other Losses/Gains (loss-ve) | Misc | 0
Base Receive Design Correction Factor: First Road |  |  | 9 | Receive Design Correction Factor: Second Road |  |  | 10
Antenna Pole Design: First Road |  |  |  | Antenna Pole Design: Second Road
| Antenna Height AGL (m) | 20 |  |  | Antenna Height AGL (m) | 10
| Selected Pole Height (m) | 15 |  |  | Selected Pole Height (m) | 10
| Pole/Mast Type | Free Standing |  |  | Pole/Mast Type | Free Standing
Design Summary: First Road |  |  | Design Summary | Design Summary: Second Road |  |  | Design Summary
| Bearing (deg) |  | 6 |  | Bearing (deg) |  | 186
| Path Length Site A to Site B (Km) |  | 4.68 |  | Path Length Site A to Site B (Km) |  | 4.68
| Antenna Height AGL (m) |  | 20 |  | Antenna Height AGL (m) |  | 10 |  | Measured/Calculated Path Losses | [5 empty] | First Road | Second Road
| Antenna Gain (dBi) |  | 8 |  | Antenna Gain (dBi) |  | 13
| Radio Power Output (dBm) |  | 33 |  | Radio Power Output (dBm) |  | 32 |  | Calculated Free Space Path Loss (dBi) | [5 empty] | 99.0851 | 98.9043
| Expected RSSI Local Site (dBm) |  | -78 |  | Expected RSSI Local Site (dBm) |  | -78 |  | Measured Path Loss @ Selected Pole Height (dBi) | [5 empty] | 124.5 | 125.5
| Expected RSSI Adjacent Site (dBm) |  | -78 |  | Expected RSSI Adjacent Site (dBm) |  | -78 |  | Measured Additional Diffraction and Other Path Losses (dB) | [5 empty] | 25.4149 | 26.5957
| Receiver Sensitivity for BER of 1.0E-6 (dBm) |  | -94 |  | Receiver Sensitivity for BER of 1.0E-6 (dBm) |  | -94
| Fade Margin Local Site (dB) |  | 16 |  | Fade Margin Local Site (dB) |  | 16 | Notes:
| Fade Margin Adjacent Site (dB) |  | 16 |  | Fade Margin Adjacent Site (dB) |  | 16 |  | Enter data or select options in white cells.
| Feeder Specification |  | LDF4-50 |  | Feeder Specification |  | LDF4-50 |  | Results are automatically calculated and entered into green cells.
| Feeder Length (m) |  | 30 |  | Feeder Length (m) |  | 20 |  | All green cells are locked.
| Antenna Specification |  | BA80 Dipole Array |  | Antenna Specification |  | YBSS9 |  | Total Feeder Length is automatically calculated: Total Feeder Length = Horizontal Feeder Length + Antenna Height.
Expected RSSI (dBm) = Measured RSSI (dBm) + DCF (dB).
| EIRP (W) |  | 4.4668 |  | EIRP (W) |  | 19.9526 |  | Select graph X and Y axes scales and legend location manually.

## Selection Lists
Cables | Loss/m (400-520) | Loss/m (806-960) | Antenna | Gain (dBi) | Group Number | Radio Type | Model Number | Sensitivity (dBm) | Data rate (kb/s) | Bandwidth | Application Notes | Values | Boolean | Pole Selection | Frequency Range | Column
<Select Cable> | 0 | 0 | <Select Antenna> | 0 |  |  | <Select Radio> | 0 |  |  |  | 0 | <Select> | Select Mast | <Frequency Range> | 2
CellFoil | 0.23 | 0.29 | BA80 Dipole Array | 8 | 1 | 4RF SR+ | 64QAM - Low gain (12.5) | -101 | 52 | 12.5 |  | 1 | Yes | Free Standing | (400-520) | 2
CNT-400 | 0.1 | 0.15 | COL7 | 5 |  |  | 64QAM - High Gain (12.5) | -103 | 45.6 | 12.5 |  | 2 | No | Roof Mount |  | 3
LDF4-50 | 0.05 | 0.07 | COL8 | 8 |  |  | 16QAM (12.5) | -102 | 40 | 12.5 |  | 3 |  | Cubicle Side Mount
LDF5-50 | 0.03 | 0.04 | Low Profile | 2 |  |  | 16QAM - Low Gain (12.5) | -106 | 23.1 | 12.5 |  | 4 |  | Cubicle Flush Mount
RG-213 | 0.165 | 0.24 | Quad Stack | 11 |  |  | 16QAM - High Gain (12.5) | -110 | 17.3 | 12.5 |  | 5 |  | Guyed
|  |  | Unity Gain | 2 |  |  | QPSK (12.5) | -106 | 20 | 12.5 |  | 6 |  | Lattice
|  |  | YBSS16 | 14 |  |  | QPSK - Low Gain (12.5) | -113 | 11.6 | 12.5 |  | 7 |  | Existing
|  |  | YBSS6 | 11 |  |  | QPSK - High Gain (12.5) | -115 | 8.7 | 12.5 |  | 8 |  | Tank Mount
|  |  | YBSS9 | 13 | 2 | 4RF SR+ | 64QAM - Low gain (25) | -97 | 103.9 | 25 |  | 9 |  | Wall Mount
[7 empty] | 64QAM - High Gain (25) | -99 | 91.2 | 25 |  | 10
[7 empty] | 16QAM (25) | -99 | 80 | 25
[7 empty] | 16QAM - Low Gain (25) | -105 | 46.2 | 25
[7 empty] | 16QAM - High Gain (25) | -105 | 34.6 | 25
[7 empty] | QPSK (25) | -107 | 40 | 25
[7 empty] | QPSK - Low Gain (25) | -110 | 23.1 | 25
[7 empty] | QPSK - High Gain (25) | -112 | 17.3 | 25
[5 empty] | 3 | 4RF SR+ | 64QAM - Low gain (50) | -94 | 187.1 | 50
[7 empty] | 64QAM - High Gain (50) | -96 | 164.2 | 50
[7 empty] | 16QAM (50) | -96 | 144 | 50
[7 empty] | 16QAM - Low Gain (50) | -102 | 83.2 | 50
[7 empty] | 16QAM - High Gain (50) | -102 | 62.4 | 50
[7 empty] | QPSK (50) | -104 | 72 | 50
[7 empty] | QPSK - Low Gain (50) | -107 | 41.6 | 50
[7 empty] | QPSK - High Gain (50) | -109 | 31.2 | 50
[5 empty] | 4 | Other | Elpro (450-470 MHz) | -108 | Licensed bands |  | Not to be used unless express permission is granted by the Principal SCADA Engineer, Operational Technology
Required RSL: | -64 | Pole Height: | 10
-64 | 1 |  | -95 | 10
-64 | 25 |  | -55 | 10
|  |  | -75 | 10
Chart Axis
Y min | -100
Y max | -50
X min | 1
X max | 25
Required Antenna Height Second Road
Note on A1: Alan Haime: Additional items can be added to the lookup list below.
Note on E1: Alan Haime: Additional items can be added to the lookup list below.
Note on J1: Alan Haime: Additional items can be added to the lookup list below.
Note on K1: Alan Haime: Additional items can be added to the lookup list below.
Note on T1: Alan Haime: Additional items can be added to the lookup list below.

## PMP Licence Details
Application for Point to Multipoint Radio Licence
"Name" Water / Wastewater Scheme
PMP base station repeater site name | First Road
Name of the structure housing the equipment eg electrical cubicle or equipment hut | RTU Cubicle
Street address of site eg 25 Smith St, Location 2435 or 400m NW of intersection . . . | 123 First Rd, Clarkesville
Geographic latitude (GDA94) | -31 20 05.00
Geographic longitude (GDA94) | 115 53 52.00
Grid easting (MGA94) | 0
Grid northing (MGA94) | 0
Grid zone (MGA) | 0
Source of coordinates eg GPS, map (details) or other means | GPS
4RF SR+ radio equipment type | 64QAM - Low gain (50)
Emission Designator | 50K0D1D
Antenna type and model | BA80 Dipole Array
Antenna height above ground level (m) | 20
Antenna support structure | Free Standing
Antenna polarisation | Vertical
Transmitter output power (dBm) | 33
Data speed (kbps) | 187.1
Radio channel bandwidth (kHz) ie 12.5kHz, 25kHz or 50kHz | 50
Frequency TX band (MHz) | 461
ACMA Client name and address | Water Corporation (WA) PO Box 100 LEEDERVILLE WA 6902
ACMA Client number | 230944
Additional information

## PP Licence Details
Application for Point to Point Radio Licence
Form Not Applicable
Item | Site A | Site B
PP site name | First Road | Second Road
Name of the structure housing the equipment eg electrical cubicle or equipment hut | RTU Cubicle | PS Building
Street address of site eg 25 Smith St, Location 2435 or 400m NW of intersection . . . | 123 First Rd Clarkesville | 345 Second Rd Clarksesville
Geographic latitude (GDA94) | -31 20 05.00 | -31 17 33.69
Geographic longitude (GDA94) | 115 53 52.00 | 115 54 09.21
Grid easting (MGA94) | 0 | 0
Grid northing (MGA94) | 0 | 0
Grid zone (MGA94) | 0 | 0
Source of coordinates eg GPS, map (details) or other means | GPS | GPS
Path length (km) | 4.68
4RF SR+ radio equipment type | 64QAM - Low gain (50) | 64QAM - Low gain (50)
Emission Designator | 50K0D1D | 50K0D1D
Antenna type and model | BA80 Dipole Array | YBSS9
Antenna height above ground level (m) | 20 | 10
Antenna support structure | Free Standing | Free Standing
Fixed loss (duplexer, feeder cable, connectors & surge suppressor, dB) | 4.5 | 2
Antenna polarisation ie horizontal (preferred) or vertical | Horizontal
Transmitter output power (dBm) | 33 | 32
Data speed (kbps) | 187.1 | 187.1
Radio channel bandwidth (kHz) ie 12.5kHz, 25kHz 50kHz | 50 | #N/A
Frequency TX band (MHz) | 461 | 451
ACMA Client name and address | Water Corporation (WA) PO Box 100 LEEDERVILLE WA 6902
ACMA Client number | 230944
Additional information | The path is badly obstructed and will require +32 dBm TX power to achieve the required fade margin. The fixed losses at each end are 2 dB or more, as shown above, and the power into the antenna will be no more than 1W.