| 1. GENERAL DATA |
| --- |
| PROJECT NAME: | PROJECT NO.: |
| DESCRIPTION: |

| 2. COOLING WATER THERMAL FLOW SWITCH | DONE /YES | NO | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- |
| Make and model |  |  |  |  |
| Zero flow set. |  |  |  |  |
| Maximum flow set. Confirm and record actual flow. |  |  |  | Flow:- Method:- |
| Noflow/flow setpoint set. |  |  |  | Setpoint:- |
| Confirm operation of flow status to PLC by starting pump. Record operating time. |  |  |  | Time for flow to establish:- |
| Throttle supply water valve. Confirm operation of no flow status to PLC. |  |  |  |  |

| 3. COOLING WATER TEMPERATURE SWTCH | DONE /YES | NO | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- |
| Make and model |  |  |  |  |
| Confirm displayed water temperature is correct. |  |  |  | Displayed:- Measured:- |
| Set high alarm set and reset points |  |  |  | Set:- Reset:- |
| Confirm operation of high alarm set and reset status to PLC by heating water in pipe. |  |  |  |  |
| Record water temperature after main pump has operated for some time. |  |  |  | kW:- Time:- Cool Temp:- Hot Temp:- |

| 4. UNIT THERMAL FLOW SWITCH | DONE /YES | NO | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- |
| Make and model |  |  |  |  |
| Max flow set. Record flow. |  |  |  | Flow:- Method:- |
| Zero flow set. |  |  |  |  |
| Noflow/flow setpoint set. Record flow. |  |  |  | Setpoint:- |
| Confirm operation of flow status to PLC by starting pump. Record Operating time. |  |  |  | Time for flow to establish:- |
| Reduce speed of pump to below setpoint. Confirm operation of no flow status to PLC. |  |  |  |  |

| 5. UNIT NOZZLE CHECK VALVE FLOW SWITCH | DONE /YES | NO | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- |
| Make and model |  |  |  |  |
| Confirm operation of flow status to PLC by starting pump. Record this flow and operating time. |  |  |  | Flow:- Time for flow to establish:- |
| Reduce speed of pump to below operating point. Confirm operation of no flow status to PLC. |  |  |  |  |

| 6. COOLING WATER PUMP | DONE /YES | NO | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- |
| Make and model |  |  |  |  |
| Confirm operating current is less than FLC. Record this current. |  |  |  | Operating Current:- FLC:- |
| Overload set and in Manual. Circuit breaker set. Record settings. |  |  |  | O/L setting:- CB Setting:- |

| 7. VENTILATION FAN & DAMPER | DONE /YES | NO | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- |
| Make and model |  |  |  |  |
| Confirm operating current is less than FLC. Record this current. |  |  |  | Operating Current:- FLC:- |
| Overload set and in Manual. Circuit breaker set. Record settings. |  |  |  | O/L setting:- CB Setting:- |
| Damper operation OK. Record time to open |  |  |  | Opening Time:- |

| 8. SUCTION PRESSURE SWITCH | DONE /YES | NO | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- |
| Make and model |  |  |  |  |
| Record settings. |  |  |  | Contact Used:- Closed (ie low suction):- Open (ie suction OK):- |
| Confirm operation to PLC by applying actual pressure. |  |  |  |  |

| 9. DELIVERY PRESSURE SWITCH | DONE /YES | NO | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- |
| Make and model |  |  |  |  |
| Record settings. |  |  |  | Contact Used:- Closed (ie delivery OK):- Open (ie high delivery):- |
| Confirm operation to VSD (process stop) by applying actual pressure. Record Delay OFF setting. |  |  |  | Timer Setting:- |

| 10. MOTOR WATER LEAK DETECTOR SWITCH AND AMPLIFIER | DONE /YES | NO | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- |
| Make and model. |  |  |  | Detector:- Rechner KAS-40-A12-N Amplifier:- Rechner N-131/2-01 |
| Confirm probe installed external to motor and completely insulated from earth. |  |  |  |  |
| Confirm probe sensitivity set to minimum required for reliable operation. |  |  |  |  |
| Confirm isolator is set for NC operation (ie contact opens on water detected). |  |  |  |  |
| Confirm operation to VSD (trip loop) by applying water to probe after installation. Record Delay OFF setting |  |  |  | Timer Setting:- |
| Confirm no false operation of sensor due to “electrical noise” at all speeds, with other pumps operating and with generator or Western Power supplies. |  |  |  |  |

11. REMARKS / REMEDIAL ACTIONS

| 12. SIGNOFFS |  |
| --- | --- |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |