1. INTRODUCTION

Refer to WC-XX-X-000-P INTRODUCTION.doc for all introductory notes regarding this procedure.

2. INSTALLATION INSPECTION

Prerequisites

1.	SUPPLY VERIFICATION (WC-SV-E-001-R LV CABLING.doc) COMPLETED

2.	CONSTRUCTION VERIFICATION (WC-CV-E-001-R LV CABLING.doc) PRESENT

Procedure

- Ensure all isolations and tagging procedures have been initiated where required or refer to HV switching program where applicable.

- Check that the cable is of correct size and type as stipulated in the cable schedule.

- Check cable identification markings are in place.

- Check cable for mechanical damage.

- Check cable glands, shrouds and locknuts are tight and have been installed correctly

- Check that cable gland plate is secure and earthed.

- Check terminations to ensure that all nuts, washers and spring washers are in place.

- Check cable termination to ensure that all lugs are crimped and terminals are clean and free of dust.

- Ensure that the HV termination kit has been installed correctly.

- Ensure earth cable has been terminated.

- Ensure cable screen has been terminated at one (appropriate) end

- Ensure that cable bending radius has not been exceeded.

- Ensure cable is terminated to meet design drawing requirements.

- Check that all terminations are tight and where torque settings are required, ensure that correct values have been obtained and connection has been marked to indicate completion.

- Check that the contact area of the lug onto the busbar or termination exceeds the cable conductor area.