1. INTRODUCTION

Refer to WC-XX-X-000-P INTRODUCTION.doc for all introductory notes regarding this procedure.

2. INSTALLATION INSPECTION

Prerequisites

1.	SUPPLY VERIFICATION (WC-SV-E-001-R LV CABLING.doc) COMPLETED

2.	CONSTRUCTION VERIFICATION (WC-CV-E-001-R LV CABLING.doc) PRESENT

Procedurebbb

- Check cable tag numbering is correct.

- Verify cable size and type is as per design drawings.

- Verify that cable installation has been completed satisfactorily, specifically with cable glands complete and tight, and cable ends made up and terminated satisfactorily.

- Ensure phasing is correct.

- Perform continuity tests on each core. This is a multi-person job and requires radios or other appropriate means of communication between the person(s) at each end of the cable.

- Disconnect cable cores at both ends (if procedure carried out post cable installation).

- Sequentially earth one end of each core and check for continuity to earth from the other end of the cable. Check for open circuit prior to and following each core to earth.  Complete corresponding test result entries in report.

- Perform insulation resistance test on each cable. Record insulation resistance. Investigate the reason for any reading below 1MΩ.

- Disconnect cable cores at both ends.

- Carry out megger insulation testing by selecting the cores indicated in each group in the following two tables, at one end of the cable and earthing all the other cores plus the screen (if applicable) at the other.

- Megger between the selected cores and earth.

Table 1 – Multi Core Cables

| Cable | Group No. |
| --- | --- |
|  | 1 | 2 | 3 | 4 | 5 |
| 1-4 core cable | 1 | 2 | 3 | 4 | E |
| 6 core cable | 1 | 2, 4, 6 | 3, 5, E |  |  |
| 8 core cable | 1 | 2, 4, 6, 8 | 3, 5, 7, E |  |  |
| 12 core cable | 1 | 2, 4, 6 | 3, 5, 7, 9, 11 | 8, 10, 12, E |  |
| 20 core cable | 1 | 2, 4, 6 | 3, 5, 7 | 8, 10, 12, 14, 16, 18, 20 | 9, 11, 13, 15, 17, 19, E |
| 30 core cable | 1 | 2, 4, 6, 20, 22, 24, 26, 28, 30 | 3, 5, 7, 21, 23, 25, 27, 29 | 8, 10, 12, 14, 16, 18 | 9, 11, 13, 15, 17, 19, E |
| 50 core cable | 1 | 2, 4, 6, 20, 22, 24, 26, 28, 30, 32, 34 | 3, 5, 7, 21, 23, 25, 27, 29, 31, 33 | 8,10,12,14,16,18,36,38,40,42,44,46,48,50 | 9,11,13,15,17,19,35,37,39,41,43,45,47,49,E |

Table 2 – Multi Pair Cables

| Cable | Group No. |
| --- | --- |
|  | 1 | 2 | 3 | 4 | 5 | 6 |
| 1 and 2 pair cables | 1B | 1W | 2B | 2W |  |  |
| 4 pair cable | 1B | 1W, 3W | 2W, 4B | 2B, 4W | 3B |  |
| 6 pair cable | 1W | 1B | 2B, 4W, 6W | 2W, 4W, 6B | 3B, 5W | 3W, 5B |
| 8 pair cable | 1W | 1B | 2W, 4B, 6B, 8B | 2B, 4W, 6W, 8W | 3W, 5B, 7B | 3B, 5W, 7W |
| 10 pair cable | 5B | 1W, 4B, 6B, 8B, 10B | 1B, 4W, 6W, 8W, 10W | 2W, 3B, 5W, 7B, 9W | 2B, 3W, 7W, 9B |  |
| 12 pair cable | 1W, 3B, 5B, 6W, 8W, 10W, 12W | 1B, 2W, 4B, 6B, 8B, 10B, 12B | 2B, 4W, 7W, 9W, 11W | 3W, 5W, 7B, 9B, 11B |  |  |
| 16 pair cable | 1W, 8W, 10B, 12B, 14B, 16B | 1B, 8W, 10W, 12W, 14W, 16W | 2W, 4B, 6W, 9W, 11W, 13W, 15W | 2B, 4W, 6B, 9B, 11B, 13B, 15B | 3B, 5W, 7W | 3W, 5B, 7B |
| 20 pair cable | 1W, 8B, 10B, 12B, 14B, 16B, 18B | 1B, 8W, 10W, 12W, 14W, 16W, 18W | 2W, 4B, 6W, 9W, 11W, 13W, 15W, 17W, 19W | 2B, 4W, 6B, 9B, 11B, 13B, 15B, 17B, 19B | 3W, 5W, 7W, 20W | 3B, 5B, 7B, 20B |

Table32 – Cables Containing Triples

|  | Group No. |
| --- | --- |
|  | 1 | 2 | 3 |
| 4 triples cable | 1W, 2R, 3B, 4B | 1B, 2B, 3W, 4W | 1R, 2W, 3R, 4R |
| 6 triples cable | 1W, 2R, 3B-6B | 1B, 2B, 3W-6W | 1R, 2W, 3R-6R |
| 12 triples cable | 1W, 2R, 3B-6B, 7W-12W | 1B, 2B, 3W-6W, 7B-12W | 1R, 2W, 3R-12R |
| 16 triples cable | 1W, 2R, 3B-6B, 7W-16W | 1B, 2B, 3W-6W, 7B-16B | 1R, 2W, 3R-6R |

- Reconnect each core at its terminal and firmly tighten.

- Upon successful completion of inspection and test procedure, affix a yellow status label around sheathing just inside cable entry to enclosure. Record any discrepancies between physical wiring and wiring diagrams on design drawings.