| Project Data |
| --- |
| PROJECT NAME: | PROJECT NO.: |
| WC PO / CONTRACT NO.: | WC ITEM / LINE NO.: |
| SITE |  |

| 1. EARTH INSTALLATION TYPE |
| --- |
| HIGH VOLTAGE | COMBINED: |
| LOW VOLTAGE: | ELECTRODES |
| OTHER: | EARTH BED |
| PROVIDE DETAILS |

| 3. TEST EQUIPMENT DETAILS |
| --- |
| MAKE: | MODEL: |
| SERIAL NUMBER: | ASSET NUMBER (if Applicable): |

| 4. TEST METHOD |
| --- |
| 61.8% RULE: | OTHER: |
| PROVIDE DETAILS |

| 5. METER CONNECTIONS |
| --- |
| FIG 3a Earth Testing Procedures | OTHER: |
| PROVIDE DETAILS |

| 6. ELECTRODE SPACING |
| --- |
| E-P2 | (m) | OTHER |  |
| P2-C2 | (m) |  |  |

| 7. TEST RESULTS |
| --- |
| Reference | Ohms | Reference | Ohms |  | Ohms |
| HV Electrode #1 |  | HV Electrode #2 |  | Total |  |
| LV Electrode #1 |  | LV Electrode #2 |  | Total |  |
| Combined #1 |  | Combined #2 |  | Total |  |
| Other #1 |  | Other #2 |  | Total |  |

| 8. TEST ENVIRONMENT |
| --- |
| SOIL MATERIAL / COMPOUND |  |
| SOIL CONDITION | DRY: |
| MOIST | WET: |
| WEATHER CONDITIONS |  |
| TEMPERATURE |  |

11. SITE DRAWING OF TEST AREA

9. REMARKS / REMEDIAL ACTIONS

| 10. SIGNOFFS |  |
| --- | --- |
| NAME (PRINT) | COMPANY / ROLE Contractors Rep | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE Clients Rep | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |

EARTH TESTER

C1 	          P1           P2        C2

E                                         P                              C

61.8%of EC                             38.2% of EC

Resistance area of earth

Tester current spike

Resistance area of earth electrode

Under test

SEPARATE EARTHING SYSTEMS;

A separate earthing system comprises two separate and distinct earthing systems; one for the high voltage electrical equipment and the other for the low voltage electrical equipment.

RESISTANCE TO EARTH; The earth connections of the earthing systems shall be located, installed and maintained so

That the resistance to earth shall not exceed the following:

- High voltage system:						30Ohms

- Low voltage system:

i)	Aggregate transformer rating up to 50kV. A:		30 Ohms

- Aggregate transformer rating over 50kV. A

But not more than 500 kV. A:			15 Ohms

iii)	Aggregate transformer rating over 500kV. A:	10 Ohms

These resistances shall be achieved independently of any connections between the neutral conductor and earth at other points within the installation.

COMBINED EARTHING SYSTEM;

A combined earthing system is one in which the voltage and low voltage electrical is earthed to a common terminal bar.

RESISTANCE TO EARTH;

The combined earthing system shall have a resistance to earth not greater than 1Ω.The resistance

Of 1 Ω, may be achieved by connections to electrode systems, metallic cable sheaths or low voltage neutrals, provided that when any such connection is temporarily removed for test or maintenance purposes the resistance of the remaining earthing connections  Does not exceed 30Ω.