| 1. GENERAL & SWITCHBOARD DATA |
| --- |
| PROJECT NAME: | PROJECT NO.: |
| SITE NAME: | SITE ADDRESS: |
| MANUFACTURER (MF): | IP RATING: |
| TYPE/MODEL: | WC DWG NO.(S): |
| SYSTEM VOLTAGE: | SERIAL NO.: |
| MF DWG NO.(S): | TYPE TEST RATING: |

| 2. SPECIFIC DATA (Arc Flash System) |
| --- |
| MANUFACTURER (MF): | IP RATING: |
| TYPE/MODEL: | WC DWG NO.(S): |
| SYSTEM VOLTAGE: | SERIAL NO.: |
| TEST DATE: |  |

| 3. INSPECTION & TEST | DONE /YES | NO | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- |
| 1 | Check wiring configuration against design drawing(s) |  |  |  |  |
| 2 | Confirm equipment lay-out as per design drawing(s) including required labels |  |  |  |  |
| 3 | Check Correct Panel Lock (if applicable) |  |  |  |  |
|  | All auxiliary equipment available for FAT test (sensors, CT’s, if required a CB) |  |  |  |  |
| 4 | Check Backup battery power/UPS supply |  |  |  |  |
| 5 | Confirm all light sensors function and display indicator LED on I/O panel |  |  |  |  |
| 6 | Confirm Current trip setting value(s) Confirm all CTs function and display on head unit Confirm all CT tests completed (polarity, primary, ratio, pick-up) |  |  |  |  |
| 7 | Verify the AFD trips correctly on current and light activation (trigger light sensors while secondary injecting current above and below current set point) |  |  |  |  |
| 8 | Verify the AFD discriminates each zone (where applicable) |  |  |  |  |
| 9 | Confirm mechanical and electrical operation for all CB to be operated by AFD system including remote operation if applicable |  |  |  |  |
| 10 | Confirm total fault clearance time does not exceed value used in calculations (eg. typically 10ms AFD + 60ms CB = 70ms) |  |  |  |  |
| 11 | Check SCADA alarm/trip signal feedback activated |  |  |  |  |
| 12 | Check Instruction provided on how to reset a fault |  |  |  |  |
| 13 | All test results recorded and saved |  |  |  |  |
| 14 | Copy and save any configuration files to MDT Autosave |  |  |  |  |

4. REMARKS / REMEDIAL ACTIONS

Arc Flash Test Results

Overall Test of Arc Flash Relay

Note: (GENERIC LOGIC)

Test the Arc Flash Relay with Light and Current Injection (As Applicable)

Using a light flash, no current or below set point injection (ACB – no trip)

Injection current above set point, no light (ACB – no trip)

Inject current above set point and using a light flash (ACB – trip)

With each CB trip, record CB timing (as applicable)

Final Settings of Arc Flash Relay

| Description | Below current Set point | Pick Up Current Set point | Total No of Sensors | No of I/O Units/modules |
| --- | --- | --- | --- | --- |
| Final Settings of AFD system |  |  |  |  |

| Metering Test (Relay Accuracy) |
| --- |
| CT Ratio: | Injected Current | IL1 | IL2 | IL3 |
| 100% Nominal | 5.0A | A | A | A |
| 50% Nominal | 2.5A | A | A | A |
| 10% Nominal | 0.5A | A | A | A |

| Current Set Point Pick-up Test |
| --- |
|  | IL1 | IL2 | IL3 | Pass/Fail |
| Pick-Up |  |  |  |  |

CT Tests

| CT No | Name Plate details of CT (ratio, etc.) | Ratio Test Pass/ Fail | Polarity Test Pass / Fail | Pick-up Test | Primary Test |
| --- | --- | --- | --- | --- | --- |

| Test Instrument Details | Serial Number | Calibration Due Date |
| --- | --- | --- |

| Sensor #: | Location | LIGHT, NO CURRENT (NO TRIP) | CURRENT, NO LIGHT (NO TRIP) | LIGHT & CURRENT (CB TRIP) | Timing | Overall Test Result (Pass / Fail) |
| --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  | Relay | CB |  |
| 1 |  |  |  |  |  |  |  |
| 2 |  |  |  |  |  |  |  |
| 3 |  |  |  |  |  |  |  |
| 4 |  |  |  |  |  |  |  |
| 5 |  |  |  |  |  |  |  |
| 6 |  |  |  |  |  |  |  |
| 7 |  |  |  |  |  |  |  |
| 8 |  |  |  |  |  |  |  |
| 9 |  |  |  |  |  |  |  |
| 10 |  |  |  |  |  |  |  |
| 11 |  |  |  |  |  |  |  |
| 12 |  |  |  |  |  |  |  |
| 13 |  |  |  |  |  |  |  |
| 14 |  |  |  |  |  |  |  |
| 15 |  |  |  |  |  |  |  |
| 16 |  |  |  |  |  |  |  |
| 17 |  |  |  |  |  |  |  |
| 18 |  |  |  |  |  |  |  |
| 19 |  |  |  |  |  |  |  |
| 20 |  |  |  |  |  |  |  |
| 21 |  |  |  |  |  |  |  |
| 22 |  |  |  |  |  |  |  |
| 23 |  |  |  |  |  |  |  |
| 24 |  |  |  |  |  |  |  |
| 25 |  |  |  |  |  |  |  |
| 26 |  |  |  |  |  |  |  |
| 27 |  |  |  |  |  |  |  |
| 28 |  |  |  |  |  |  |  |
| 29 |  |  |  |  |  |  |  |
| Sensor #: | Location | LIGHT, NO CURRENT (NO TRIP) | CURRENT, NO LIGHT (NO TRIP) | LIGHT & CURRENT (CB TRIP) | Timing | Overall Test Result (Pass / Fail) |
|  |  |  |  |  | Relay | CB |  |
| 30 |  |  |  |  |  |  |  |
| 31 |  |  |  |  |  |  |  |
| 32 |  |  |  |  |  |  |  |
| 33 |  |  |  |  |  |  |  |
| 34 |  |  |  |  |  |  |  |
| 35 |  |  |  |  |  |  |  |
| 36 |  |  |  |  |  |  |  |
| 37 |  |  |  |  |  |  |  |
| 38 |  |  |  |  |  |  |  |
| 39 |  |  |  |  |  |  |  |
| 40 |  |  |  |  |  |  |  |
| 41 |  |  |  |  |  |  |  |
| 42 |  |  |  |  |  |  |  |
| 43 |  |  |  |  |  |  |  |
| 44 |  |  |  |  |  |  |  |
| 45 |  |  |  |  |  |  |  |
| 46 |  |  |  |  |  |  |  |
| 47 |  |  |  |  |  |  |  |
| 48 |  |  |  |  |  |  |  |
| 49 |  |  |  |  |  |  |  |
| 50 |  |  |  |  |  |  |  |
| 51 |  |  |  |  |  |  |  |
| 52 |  |  |  |  |  |  |  |
| 53 |  |  |  |  |  |  |  |
| 54 |  |  |  |  |  |  |  |
| 55 |  |  |  |  |  |  |  |
| 56 |  |  |  |  |  |  |  |
| 57 |  |  |  |  |  |  |  |
| 58 |  |  |  |  |  |  |  |
| Sensor #: | Location | LIGHT, NO CURRENT (NO TRIP) | CURRENT, NO LIGHT (NO TRIP) | LIGHT & CURRENT (CB TRIP) | Timing | Overall Test Result (Pass / Fail) |
|  |  |  |  |  | Relay | CB |  |
| 59 |  |  |  |  |  |  |  |
| 60 |  |  |  |  |  |  |  |

Comments:

Average Trip Time = ms

Assessment of Overall AFD Scheme - Pass / Fail

| 5. SIGNOFFS |  |
| --- | --- |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |