| 1. GENERAL & SWITCHBOARD DATA |
| --- |
| PROJECT NAME: | PROJECT NO.: |
| SITE NAME: | SITE ADDRESS: |
| MANUFACTURER (MF): | IP RATING: |
| TYPE/MODEL: | WC DWG NO.(S): |
| SYSTEM VOLTAGE: | SERIAL NO.: |
| MF DWG NO.(S): | TYPE TEST RATING: |

| 2. SPECIFIC DATA (Arc Flash System) |
| --- |
| MANUFACTURER (MF): | IP RATING: |
| TYPE/MODEL: | WC DWG NO.(S): |
| SYSTEM VOLTAGE: | SERIAL NO.: |
| TEST DATE: |  |

| 3. INSPECTION & TEST | DONE /YES | NO | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- |
| 1 | Design/Mark up drawings Available for use |  |  |  |  |
| 2 | Installation of AFD Panel/equipment complete as per approved drawings |  |  |  |  |
| 3 | Installation of All AFD Sensors in SB complete as per approved design drawings/locations, labelled, wiring back to AFD relay/panel complete |  |  |  |  |
| 4 | Installation of MCB/Fuse in SL&P DB complete and labelled |  |  |  |  |
| 5 | Installation of all AFD CT’s complete as per design drawings (location & fixings) |  |  |  |  |
| 6 | CT tests completed and recorded (polarity, primary, ratio) |  |  |  |  |
| 7 | Installation of New ACB with Retrofit kit complete (if applicable) |  |  |  |  |
| 8 | CB tests complete and recorded (primary, secondary, insulation, contact resistance, CB timing) |  |  |  |  |
| 9 | Installation of Wiring/cabling between AFD Panel and SL&P DB complete, labelled, tested and connected Cable test complete and recorded - @ 500vdc (AS3000) |  |  |  |  |
| 10 | Installation of Wiring//cabling between AFD Panel and SCADA Panel complete, labelled and connected |  |  |  |  |
| 11 | Installation of wiring/cabling between AFD panel and AFD CT’s complete, labelled and connected |  |  |  |  |
| 12 | Installation of wiring/cabling from AFD panel to CB complete, labelled and connected (if applicable) |  |  |  |  |
| 13 | Installation of any CB coils (open/close) complete (as required) |  |  |  |  |
| 14 | CB mechanical alignment and operation confirmed as required (rack in/out, CB open/close) |  |  |  |  |
| 15 | CB electrical operation confirmed as required (motor spring charge, CB open/close) |  |  |  |  |
| 16 | CB remote operation and indication confirmed as required (open/close) |  |  |  |  |
| 17 | CB “remote operation available” label fitted (DS29) |  |  |  |  |
| 18 | All other mitigation works complete as per Scope Of Works for the site |  |  |  |  |
| 19 | Arc Flash Detection Relay powered up and all Indications correct/normal (no alarms) |  |  |  |  |
| 20 | Check configuration and settings on Arc Flash Relay to be appropriate for plant/station including current set point |  |  |  | Reference site file # |
| 21 | Perform commissioning of arc flash system using the designed logic for the site |  |  |  |  |
| 22 | CB timing recorded for each sensor tested (≤ 70ms or otherwise stated) |  |  |  |  |
| 23 | AFD Power Supply – from battery backed sourced (AFD trip indication still available after Main CB tripped) |  |  |  |  |
| 24 | Fault reset – test and ensure system is ready to trip again |  |  |  |  |
| 25 | Confirmed with Scada Helpdesk when each alarm/trip signal is triggered, their system can see it. |  |  |  |  |
| 26 | All Test results recorded |  |  |  |  |
| 27 | Take photos of Installation (Sensors, CT’s, ACB, Cable ducts, AFD Panel etc.) |  |  |  |  |
| 28 | Red line drawings - Leave 1 copy in Switchboard for operators and return 1 copy to Project Team. Design/Mark up drawings Available for use and left in panel |  |  |  |  |
| 29 | Update code in MDT Autosave if changed |  |  |  |  |

4. REMARKS / REMEDIAL ACTIONS

Arc Flash Test Results (see below)

Overall Test of Arc Flash Relay

Note: (GENERIC LOGIC)

Test the Arc Flash Relay with Light and Current Injection (As Applicable)

Using a light flash, no current or below set point injection (ACB – no trip)

Injection current above set point, no light (ACB – no trip)

Inject current above set point and using a light flash (ACB – trip)

With each ACB trip, record ACB timing

Final Settings of Arc Flash Relay

| Description | Below current Set point | Pick Up Current Set point | Total No of Sensors | No of I/O Units/modules |
| --- | --- | --- | --- | --- |
| Final Settings of AFD system |  |  |  |  |

CT Tests

| CT No | Name Plate details of CT (ratio, etc.) | Ratio Test Pass/ Fail | Polarity Test Pass / Fail | Pick-up Test | Primary Test |
| --- | --- | --- | --- | --- | --- |

| Test Instrument Details | Serial Number | Calibration Due Date |
| --- | --- | --- |

| Sensor #: | Location | LIGHT, NO CURRENT (NO TRIP) | CURRENT, NO LIGHT (NO TRIP) | LIGHT & CURRENT (CB TRIP) | ACB TIMING (Ms) | Overall Test Result (Pass / Fail) |
| --- | --- | --- | --- | --- | --- | --- |
| 1 |  |  |  |  |  |  |
| 2 |  |  |  |  |  |  |
| 3 |  |  |  |  |  |  |
| 4 |  |  |  |  |  |  |
| 5 |  |  |  |  |  |  |
| 6 |  |  |  |  |  |  |
| 7 |  |  |  |  |  |  |
| 8 |  |  |  |  |  |  |
| 9 |  |  |  |  |  |  |
| 10 |  |  |  |  |  |  |
| 11 |  |  |  |  |  |  |
| 12 |  |  |  |  |  |  |
| 13 |  |  |  |  |  |  |
| 14 |  |  |  |  |  |  |
| 15 |  |  |  |  |  |  |
| 16 |  |  |  |  |  |  |
| 17 |  |  |  |  |  |  |
| 18 |  |  |  |  |  |  |
| 19 |  |  |  |  |  |  |
| 20 |  |  |  |  |  |  |
| 21 |  |  |  |  |  |  |
| 22 |  |  |  |  |  |  |
| 23 |  |  |  |  |  |  |
| 24 |  |  |  |  |  |  |
| 25 |  |  |  |  |  |  |
| 26 |  |  |  |  |  |  |
| 27 |  |  |  |  |  |  |
| 28 |  |  |  |  |  |  |
| 29 |  |  |  |  |  |  |
| Sensor #: | Location | LIGHT, NO CURRENT (NO TRIP) | CURRENT, NO LIGHT (NO TRIP) | LIGHT & CURRENT (CB TRIP) | ACB TIMING (Ms) | Overall Test Result (Pass / Fail) |
| 30 |  |  |  |  |  |  |
| 31 |  |  |  |  |  |  |
| 32 |  |  |  |  |  |  |
| 33 |  |  |  |  |  |  |
| 34 |  |  |  |  |  |  |
| 35 |  |  |  |  |  |  |
| 36 |  |  |  |  |  |  |
| 37 |  |  |  |  |  |  |
| 38 |  |  |  |  |  |  |
| 39 |  |  |  |  |  |  |
| 40 |  |  |  |  |  |  |
| 41 |  |  |  |  |  |  |
| 42 |  |  |  |  |  |  |
| 43 |  |  |  |  |  |  |
| 44 |  |  |  |  |  |  |
| 45 |  |  |  |  |  |  |
| 46 |  |  |  |  |  |  |
| 47 |  |  |  |  |  |  |
| 48 |  |  |  |  |  |  |
| 49 |  |  |  |  |  |  |
| 50 |  |  |  |  |  |  |
| 51 |  |  |  |  |  |  |
| 52 |  |  |  |  |  |  |
| 53 |  |  |  |  |  |  |
| 54 |  |  |  |  |  |  |
| 55 |  |  |  |  |  |  |
| 56 |  |  |  |  |  |  |
| 57 |  |  |  |  |  |  |
| 58 |  |  |  |  |  |  |
| Sensor #: | Location | LIGHT, NO CURRENT (NO TRIP) | CURRENT, NO LIGHT (NO TRIP) | LIGHT & CURRENT (CB TRIP) | ACB TIMING (Ms) | Overall Test Result (Pass / Fail) |
| 59 |  |  |  |  |  |  |
| 60 |  |  |  |  |  |  |

Record complete AFD Scheme Trip Time

Trip Time Recorded from Arc Fault Initiation to ACB trip - ms

Assessment of Overall AFD System - Pass / Fail

| 5. SIGNOFFS |  |
| --- | --- |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |