Prerequisites

1.	SUPPLY VERIFICATION (WC-SV-I-005-R PRESSURE SWITCH.doc) COMPLETED

2.	CONSTRUCTION VERIFICATION (WC-CV-I-005-R PRESSURE SWITCH.doc) 				COMPLETED

3.	PRE-COMMISSIONING (WC-PC-I-005-R PRESSURE SWITCH.doc) PRESENT

4.	Safety requirements have been complied with

5.	Final connection after piping system purging

6.	Cable continuity checks completed

WARNING:  The instrumentation contractor must be at all times aware of the scope of instrumentation work being carried out.  In particular, the instrument engineer must do the following:

- Co-ordinate the work.

- Ensure that all team members (project commissioning, vendors, and contractor personnel) follow the safety tagging and permit to work system procedures to minimise the danger to all site personnel.

WARNING:  Ensure that each circuit is complete and safe to energise before operating any circuit breakers.  Also check that the circuit breaker is correctly rated for the instrumentation it is protecting.  Energisation of incomplete installations may cause personal injury or death.

  - Pressure test the pressure switch impulse lines at 1.5 x maximum service pressure.  Take care to ensure that the pressure switch is not damaged by the impulse line test pressure.

  - Leak check the impulse lines and the pressure switch connections at the normal maximum service pressure

  - Check field marshalling terminal links in the PLC cabinet are closed.

  - Connect portable pressure source and gauge to switch and pressurise the switch to about its calibrated operating point.

  - Establish radio contact with the microSCADA/SCX Engineer or operator at the microSCADA/SCX Screen.

  - Using a certified pressure calibration device operate the pressure switch and check correct responses/indications are received by the PLC/microSCADA/SCX Screen.

  - In conjunction with microSCADA/SCX engineer, check correct operation of any indications, controls, and alarms associated with the loop.

  - Upon completion, check all links and connections are tight and enclosure is secure.

  - Carry out drawing as-built by annotating the wiring diagram in red pen to clearly show how the circuit is actually wired up where this differs from the drawing.  Ensure that any such differences are accounted for, and investigate further if this is not the case.  Annotate the drawing by hand as 'As Built', and record your name and the date.

  - Apply red marking to marshalling panel and disconnect terminals to show completion of loop test.  If remedial action on the microSCADA/SCX Screen is required note this on the report.

  - When inspection has been successfully completed and any remedial actions performed as required, affix a green status label to instrument cover to indicate completion of pre-commissioning.

| 1. GENERAL DATA |
| --- |
| PROJECT NAME: |
| PROJECT NO.: |
| WC P.O. NO.: | LINE NO.: |

| 2. PRESSURE SWITCH DATA |
| --- |
| MANUFACTURER (MF): | VENDOR DATA SHEET SUPPLIED? |
| MODEL NO.: | SERIAL NO.: |
| MF PRESSURE SWITCH NO.: | MF DWG NO.: |
| WC PRESSURE SWITCH NO.: | WC DWG NO.: |
| RANGE: | ELECTRICAL CONN. |
| DIFFERENTIAL: | DIAPHRAGM SEAL: |
| PROCESS CONN.: | FLANGE MTRL: |
| CAPILLARY MTRL: | CAPILLARY LENGTH: |
| HAZARDOUS AREA CERT.: YES NO |

| 3. TEST | DONE /YES | NO | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- |
| 3.1 Preliminary |
| Marshalling terminal links closed |  |  |  |  |
| Pressure source connected |  |  |  |  |
| Radio contact established with microSCADA/SCX Engineer |  |  |  |  |
| 3.2 SCX/microSCADA Checks |  |  |  |  |
| Instrument Tag No. correct on microSCADA/SCX Screen |  |  |  |  |
| Switch action detected at microSCADA/SCX Screen |  |  |  |  |
| Sense correct |  |  |  |  |
| Alarm and trip functions operate correctly |  |  |  |  |
| Alarm messages and logs correct |  |  |  |  |

| 4. COMPLETION | DONE /YES | NO | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- |
| Loop drawing as built? |  |  |  |  |
| Terminals tight and enclosure secure? |  |  |  |  |
| Loop left energised? |  |  |  |  |
| Green tag affixed signifying the successful completion of pre-commissioning and any remedial actions? |  |  |  |  |

5. REMARKS / REMEDIAL ACTIONS

| 6. SIGNOFFS |  |
| --- | --- |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |