| 1. GENERAL DATA |
| --- |
| PROJECT NAME | PROJECT NO |
| WC P.O. / CONTRACT NO | LINE / ITEM NO |

| 2. MOTOR DATA |
| --- |
| Make |  | KVA |  |
| Serial no |  | Voltage |  |
| Type/model |  | Current |  |
| Frame |  | Frequency |  |
| Enclosure |  | Speed |  |
| Insulation class |  | Battery voltage |  |
| Cooling |  | Engine type |  |

| 3. | VISUAL INSPECTION | YES | NO | N/A | COMMENTS |
| --- | --- | --- | --- | --- | --- |
|  | The Generating Set has been properly fixed on a common steel section base frame |  |  |  |  |
|  | Protection screen has been provided on all moving parts. |  |  |  |  |
|  | The fresh-water-cooled radiator has been properly fixed and there is no water leakage. |  |  |  |  |
|  | The radiator cooling fins and water tank are in good condition and properly fixed. |  |  |  |  |
|  | The engine mounted instrument panel has been fixed properly and c/w lubrication oil temp. And cooling temp. Gauges, tachometer and hour meter. |  |  |  |  |
|  | The lubrication oil system with replaceable element types filter has been properly fixed |  |  |  |  |
|  | Generator earth cables installed correctly. |  |  |  |  |
|  | Generator Winding RTDs cables installed correctly. |  |  |  |  |
|  | Oil temperature & oil pressure instrumentation cables installed correctly. |  |  |  |  |
|  | Confirm fuel level gauge installed |  |  |  |  |
|  | Starting batteries have been provided and properly installed |  |  |  |  |

| 4. | PRE COMMISSIONING INSPECTION DIESEL ENGINE | YES | NO | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- | --- |
|  | Radiator water is at right level |  |  |  |  |
|  | Lubrication oil is at right level and with replaceable filter |  |  |  |  |
|  | The engine exhaust has been properly fixed and covered with asbestos-fee insulation. |  |  |  |  |
|  | The engine anti-vibration mounting is effective |  |  |  |  |
|  | Proper replaceable air filter has been installed |  |  |  |  |
|  | Effective and adequate earth bonding have been provided for the engine and alternator. |  |  |  |  |
| 5. | PRE COMMISSIONING INSPECTION ALTERNATOR | YES | NO | N/A | COMMENTS/DETAILS |
|  | Batteries electrolyte is at right level |  |  |  |  |
|  | Batteries output voltage is as specified |  |  |  |  |
|  | The alternator output terminal is at correct phase sequence |  |  |  |  |

| 6. | PRE COMMISSIONING INSPECTION CONTROL CUBICAL | YES | NO | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- | --- |
| The following devices are provided in the control cubicle |
|  | Voltmeter & selector switch |  |  |  |  |
|  | Ammeter & selector switch |  |  |  |  |
|  | Frequency meter |  |  |  |  |
|  | Wattmeter |  |  |  |  |
|  | Auto/off/manual selector switch |  |  |  |  |
|  | Start/stop push button |  |  |  |  |
|  | All control wirings are fitted with ferrules |  |  |  |  |
|  | Simulate main failure” key switch |  |  |  |  |
|  | On-off” switch for generator anti-condensation element |  |  |  |  |
|  | Automatic 2 rate battery charging equipment c/w charging rate ammeter |  |  |  |  |
|  | Indicating lamp & reset button for Engine fault |  |  |  |  |
|  | Indicating lamp & reset button for Failure to start |  |  |  |  |
|  | Indicating lamp & reset button for Generator supply available |  |  |  |  |
|  | Indication lamp for Mains available |  |  |  |  |
|  | Indication lamp for Generator on load |  |  |  |  |
|  | Indication lamp for Load supplied from mains |  |  |  |  |
|  | Indication lamp for low fuel capacity |  |  |  |  |

| 7. | FUNCTIONAL TEST |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Control Function Test | Function Test | Setting | Remarks |
| a. Starting | Manual |  |  |  |
|  | Simulate Mains Failure | Test 1* |  |  |  |
|  |  | Test 2** |  |  |  |
|  | Delay Start Timer |  |  |  |
|  | Delay Repeat Start |  |  |  |
| b. Stopping | Manual |  |  |  |
|  | Resumption of Mains *** |  |  |  |
|  | Delay Stop Timer **** |  |  |  |
| c. Engine Protection | Overload Trip (MCCB) |  |  |  |
|  | Engine Overspeed | HL |  |  |  |
|  |  | LL |  |  |  |
|  | Low Lub-oil Pressure (kPa) | HL |  |  |  |
|  |  | LL |  |  |  |
|  | Low Fuel cut-out | LL |  |  |  |
|  | High Water Temp (oC | HL |  |  |  |
|  | Under Voltage Trip |  |  |  |
|  | Overvoltage Trip |  |  |  |
|  | Under Frequency (Hz) |  |  |  |
| 7. | FUNCTIONAL TEST |  |  |  |  |
| d. Others |  |  |  |  |

8. REMARKS / REMEDIAL ACTIONS

| 9. SIGNOFFS |  |
| --- | --- |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |