Procedure

- Check instrumentation is correctly installed in regard to:

- Plant location and identification.

- Process connections and attachments.

- Orientation.

- Installation, mounting and workmanship.

- Any associated items as required.

- Other items indicated on the test record sheet.

- After supply and signal cable continuity checks are completed and cables terminated, check instrument and sensor cables and wiring are connected in accordance with the hookup and loop drawings. Carefully check for correct polarity, voltage and earthing arrangements. Ensure that where cable shields are shown as not being connected they are properly insulated against contact with ground.

- Record satisfactory installation, checking off all applicable items.

- When inspection has been successfully completed and any remedial actions performed as required, affix a yellow status label to the instrument cover to indicate completion of construction verification checks.

| 1. GENERAL DATA |
| --- |
| PROJECT NAME: |
| PROJECT NO.: |
| WC P.O. NO.: | LINE NO.: |

| 2. FLOW SWITCH DATA |
| --- |
| MANUFACTURER (MF): | VENDOR DATA SHEET SUPPLIED? |
| MODEL NO.: | SERIAL NO.: |
| MF FLOW SWITCH NO.: | MF DWG NO.: |
| WC FLOW SWITCH NO.: | WC DWG NO.: |

| 3.1 SENSOR DATA – All data to be recorded if data sheet not available |
| --- |
| MODEL NO.: | SERIAL NO.: |
| PROCESS CONN: |

| 3.2 CONTROL MONITOR DATA – All data to be recorded if data sheet not available |
| --- |
| MODEL NO.: | SERIAL NO.: |
| SWITCH FORM: | POWER SUPPLY: |
| HAZARDOUS AREA CERT.: YES NO |

| 4. INSTALLATION INSPECTION | DONE /YES | NO | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- |
| 1 | Point to point testing successfully completed? |  |  |  |  |
| 2 | Location correct? |  |  |  |  |
| 3 | Orientation correct? |  |  |  |  |
| 4 | Cable checks correct – wires terminated? |  |  |  |  |
| 5 | Sun enclosure installed as per documentation |  |  |  |  |
| 6 | Installation in accordance with Specification |  |  |  |  |
| 7 | Process connection correct? |  |  |  |  |
| 8 | Earthing correct? |  |  |  |  |
| 9 | Polarity correct? |  |  |  |  |
| 10 | Yellow tag affixed signifying the successful completion of construction verification checks and any remedial actions? |  |  |  |  |

5. REMARKS / REMEDIAL ACTIONS

| 6. SIGNOFFS |  |
| --- | --- |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |