Procedure

- Remove any packing and shipping stops.

- Confirm that supplied instrument conforms to data sheet.  Record all details if data sheet not available, and advise the discipline engineer.

- If instrument is not stamped with its tag number, stamp the required tag number onto the data plate or instrument tag, following consultation with the discipline engineer.

- Set the flow switch at the setting given in the instrument specification.

- Supply correct voltage to flow switch.

- Allow for warm up time as per manufacturers recommendations.

- Use an appropriate operating method to cause the instrument to positively operate and record the result.  Record test device used on test sheet.

- Check correct operation for each type of contact fitted with a continuity tester.

- After testing, seal all connections and entries to prevent the ingress of moisture and dirt.

- If appropriate, check that the flange faces are clean (prior to fitting) and are free from any defects resulting from corrosion or any other causes.

| 1. GENERAL DATA |
| --- |
| PROJECT NAME: |
| PROJECT NO.: |
| WC P.O. NO.: | LINE NO.: |

| 2. FLOW SWITCH DATA |
| --- |
| MANUFACTURER (MF): | VENDOR DATA SHEET SUPPLIED? |
| MODEL NO.: | SERIAL NO.: |
| MF FLOW SWITCH NO.: | MF DWG NO.: |
| WC FLOW SWITCH NO.: | WC DWG NO.: |

| 3.1 SENSOR DATA – All data to be recorded if data sheet not available |
| --- |
| MODEL NO.: | SERIAL NO.: |
| PROCESS CONN: |

| 3.2 CONTROL MONITOR DATA – All data to be recorded if data sheet not available |
| --- |
| MODEL NO.: | SERIAL NO.: |
| SWITCH FORM: | POWER SUPPLY: |
| HAZARDOUS AREA CERT.: |  |

| 4. INSPECTION | DONE /YES | NO | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- |
| 4.1 General |
| 1 | Remove and retain protective covers |  |  |  |  |
| 2 | Tag stamped correctly on instrument |  |  |  |  |
| 3 | Instruction manual reviewed |  |  |  |  |
| 4.2 Bench Test and Calibration |
| 1 | Supply voltage correct |  |  |  |  |
| 2 | Warm up period allowed |  |  |  |  |
| 3 | Instrument configured per datasheet |  |  |  |  |
| 4 | Output contacts operating correctly |  |  |  |  |
| 4.3 Completion |
| 1 | Entries sealed |  |  |  |  |
| 2 | Unit protected for storage |  |  |  |  |

5. REMARKS / REMEDIAL ACTIONS

| 6. SIGNOFFS |  |
| --- | --- |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |