**Referenced to Water Corporation Standards: DS26-05, DS26-27 AND DS26-45.**

|  |
| --- |
| **1. GENERAL DATA** |
| PROJECT NAME: | PROJECT NO: |
| IDENTIFICATION: |  |

|  |
| --- |
| **2. GENERATOR DATA** |
| MAKE: | KW/KVA: |
| SERIAL NO: | VOLTAGE: |
| TYPE/MODEL: | CURRENT: |
| FRAME: | FREQUENCY: |
| ENCLOSURE PROTECTION: | SPEED: |
| COOLING: | BATTERY VOLTAGE: |
| INSULATION CLASS: | ENGINE TYPE: |

|  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| **3.** | **INSPECTION DIESEL ENGINE** | **YES** | **NO** | **N/A** | **COMMENTS** |
| 1 | Radiator water is at correct level. | [ ]  | [ ]  | [ ]  |  |
| 2 | Lubrication oil is at correct level and with replaceable filter. | [ ]  | [ ]  | [ ]  |  |
| 3 | Proper replaceable air filter has been installed. | [ ]  | [ ]  | [ ]  |  |

|  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| **4.** | **INSPECTION ALTERNATOR** | **YES** | **NO** | **N/A** | **COMMENTS** |
| 1 | Batteries electrolyte is at correct level. | [ ]  | [ ]  | [ ]  |  |
| 2 | Batteries output voltage is as specified. | [ ]  | [ ]  | [ ]  |  |
| 3 | The alternator output terminal is at correct phase sequence. | [ ]  | [ ]  | [ ]  |  |

| **5. TEST PROCEDURE** | **YES** | **NO** | **N/A** | **COMMENTS** |
| --- | --- | --- | --- | --- |
| 1 | Record cold winding and engine temperatures - confirm as expected.  | [ ]  | [ ]  | [ ]  |  |
| 2 | Magger Generator including a Polarisation Index – confirm acceptable. | [ ]  | [ ]  | [ ]  |  |
| 3 | Check all switches and indicators on switchboard function correctly. | [ ]  | [ ]  | [ ]  |  |
| 4 | Energise Anti-Condensation Heaters and record winding temperatures after 24hrs. | [ ]  | [ ]  | [ ]  |  |
| 5 | Test oil pressure fault and water temperature fault. | [ ]  | [ ]  | [ ]  |  |
| 6 | Test Failure to start, over speed and low fuel level warning fault. | [ ]  | [ ]  | [ ]  |  |
| 7 | Test general alarm, general fault and charging alternator fault. | [ ]  | [ ]  | [ ]  |  |
| 8 | Run Generator no-load one hour. Record Volts, Amps, Power, and bearing/winding temperatures – confirm as expected. | [ ]  | [ ]  | [ ]  |  |
| 9 | After running 4hour record winding temp and engine temp. | [ ]  | [ ]  | [ ]  | Engine Temp\_\_\_\_\_\_\_\_\_\_\_\_ |
| 10 | Confirm ATS connection and delay settings (phase sequence). | [ ]  | [ ]  | [ ]  |  |
| 11 | Confirm ATS functional test. | [ ]  | [ ]  | [ ]  |  |

|  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| **6.** | **FUNCTIONAL TEST** |  |  |  |  |
| Control Function Test | Function Test | Setting | Remarks |
| a. Starting | Manual |  |  |  |
| Simulate MainsFailure | Test 1 |  |  |  |
| Test 2 |  |  |  |
| Delay Start Timer |  |  |  |
| Delay Repeat Start |  |  |  |
| b. Stopping | Manual |  |  |  |
| Resumption of Mains  |  |  |  |
| Delay Stop Timer |  |  |  |
| c. Engine Protection | Overload Trip (MCCB) |  |  |  |
| EngineOverspeed | HL |  |  |  |
| LL |  |  |  |
| Low Lube-OilPressure (kPa) | HL |  |  |  |
| LL |  |  |  |
| Low Fuel cut-out | LL |  |  |  |
| High WaterTemp **(ºC)**  | HL |  |  |  |
|  |  |  |  |
| Under Voltage Trip |  |  |  |
| Overvoltage Trip |  |  |  |
| Under Frequency (Hz) |  |  |  |

|  |
| --- |
| **7. TESTS** |
| 7.1 Test Equipment |
| Megger |
| Manufacturer: | Model: |
| Serial No.: | Last Calibration Date: |
| Multimeter |
| Manufacturer: | Model: |
| Serial No.: | Last Calibration Date: |
|  |
| 7.2 Insulation Resistance Test |
| **Circuit Description** | **Stator (1000V) 1min** | **Stator (1000V) 10 min** | **Heaters (500V)** |
| **Resistance (Ω)** |  |  |  |
| **Polarisation Index** |  |  |
|  |
| 7.3 Winding RTD Measurements |
| **Description** | **Ambient** | **UØ** | **VØ** | **WØ** | **U1Ø**  | **V1Ø** | **W1Ø** |
| **Temp (ºC) – Cold** |  |  |  |  |  |  |  |
| **Temp (ºC) – Heaters 24 Hours** |  |  |  |  |  |  |  |
| **Temp (ºC) – 1 Hour No Load**  |  |  |  |  |  |  |  |
| **Temp (ºC) – 4 Hours** |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
|  |
| 7.4 Bearing RTD Measurements |
| **Description** | **Ambient** | **DE Alternator** | **NDE Alternator** | **DE Engine** | **NDE Engine** |
| **Temp (ºC) – Cold** |  |  |  |  |  |
| **Temp (ºC) – Heaters 24 Hours** |  |  |  |  |  |
| **Temp (ºC) – 1 Hour No Load**  |  |  |  |  |  |
|  |
| 7.5 Bearing Measurements |
| **Description** | **DE Alternator** | **NDE Alternator** |  |
| **Stationary** |  |  |  |
| **No Load** |  |  |  |
|  |
| 7.6 Generator Measurements |
| **Description** | **Volts** | **Amps** | **Power (kW)** |
| **No Load** |  |  |  |

|  |
| --- |
| **8. REMARKS / REMEDIAL ACTIONS** |
|  |
|  |
|  |
|  |
|  |
|  |
|  |
|  |
|  |
|  |
|  |
|  |
|  |
|  |
|  |
|  |
|  |
|  |
|  |
|  |
|  |
|  |
|  |

|  |  |
| --- | --- |
| **9. SIGNOFFS** |  |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |