| 1. GENERAL DATA |
| --- |
| PROJECT NAME: | PROJECT NO.: |

| 2. HV SWITCHBOARD DATA |
| --- |
| BOARD NAME: | MODULE NAME: |
| MANUFACTURER (MF): | TYPE: |
| SYSTEM VOLTAGE: | IP RATING: |
| MF DWG NO.(S): | WC DWG NO.(S): |

| 3. INSPECTION & TEST | DONE /YES | NO | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- |
| 1 | Main circuit resistance tested & results attached. |  |  |  |  |
| 2 | Earth switch resistance tested & results attached. |  |  |  |  |
| 3 | Power frequency voltage test completed & results attached. |  |  |  |  |
| 4 | Voltage indicating neon operation successfully checked on a “per phase” basis during item 3 above. |  |  |  |  |
| 5 | VT primary and secondary wiring checked and tested for secondary short circuit faults. |  |  |  |  |
| 6 | CT primary orientation and secondary wiring checked for correctness. |  |  |  |  |
| 7 | 24V DC tripping supply and batteries confirmed to operate correctly. |  |  |  |  |
| 8 | Protection relay tested by secondary injection with WC settings & results attached. Physical trip of circuit breaker confirmed. |  |  |  |  |
| 9 | Protection relay tested by primary injection with WC settings & results attached. Physical trip of circuit breaker confirmed. |  |  |  |  |
| 10 | Correct operation and programming of SEPAM relay confirmed and final programmed saved and electronic and paper copy attached. |  |  |  |  |
| 11 | Mechanical operation of all switches, earth switches, disconnectors, circuit breakers (including visual checks through viewing ports) and interaction with interlocks and covers verified. |  |  |  |  |
| 12 | Circuit breaker and changeover switch electric spring charging confirmed. |  |  |  |  |
| 13 | Circuit breaker undervoltage release confirmed. |  |  |  |  |
| 14 | Auto/manual electrical controls of circuit breaker & changeover switches (including those associated with generators and VSDs) confirmed. |  |  |  |  |
| 15 | Phase failure relays control of Generator/changeover switches confirmed. |  |  |  |  |
| 16 | All status indications back to PLC confirmed. |  |  |  |  |
| 17 | Ensure all required AC and DC control circuit breakers are on prior to HV energisation. Confirm current draw is as expected. |  |  |  |  |
| 18 | Record metering voltages and confirm phase rotation correct when switchboard energised. |  |  |  | R-W= W-B= B-R= R-N= W-N= B-N= R-E= W-E= B-E= |
| 19 | Confirm all metering indications on SEPAM relay and Powerlogic meter consistent with others and correct. |  |  |  |  |

4. REMARKS / REMEDIAL ACTIONS

| 5. SIGNOFFS |  |
| --- | --- |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |