| 1. SITE COMMISSIONING SHEET -MINOR SEWERAGE P/S – ELECTRICAL Page 1 of 2 |
| --- |
| PROJECT: |
| LOCATION: |
| REF DRAWINGS: |
| CHECKLIST |
|  | Y | N | N/A | COMMENTS |
| 1. FAT SHEET SUPPLIED FOR PANEL |  |  |  |  |
| 2. SAT SHEET SUPPLIED FOR PANEL |  |  |  |  |
| 3. SUPPLY INSTALLED SATISFACTORY |  |  |  |  |
| 4. U/G CONDUITS INSTALLED SATISFACTORY |  |  |  |  |
| 5. EARTH SYSTEM INSTALLED SATISFACTORY |  |  |  |  |
| 6. EARTH BONDING (PIPES) SATIFACTORY |  |  |  |  |
| 7. CIRCUIT BREAKER SETTINGS TO SPECIFICATION |  |  |  |  |
| 8. OVERLOADS SET TO SPECIFICATIONS |  |  |  |  |
| 9. MOTOR POWER CABLES INSTALLED SATISFACTORY |  |  |  |  |
| 10. CABLE SUPPORTS SATISFACTORY |  |  |  |  |
| 11. CIRCUIT DRAWINGS ON SITE |  |  |  |  |
| 12. ELECTRICAL TEST SHEETS SUPPLIED (FAT , SAT , EARTH ) |  |  |  |  |
| 13. MEGGER MOTOR – (CONFIRM ACCEPTABLE ) |  |  |  | INSUL. LEVEL = Mohm |
| 14. CHECK PUMP SUPPLY VOLTAGE AT CONVENIENT TERMINAL NEAR SUMP PUMP OR SWITCHBOARD R - N = W – N = B – N = |  |  |  | R – W = VAC R - B = VAC W – B = VAC |
| 15. FLICK TEST PUMP AND CHECK ROTATION DIRECTION |  |  |  |  |
| 16. CONFIRM ALARM LEVEL HIGH FLOAT TO OPS. CENTRE |  |  |  |  |
| 17. RECORD PUMP RUNNING CURRENTS PUMP No1 PUMP No2 |  |  |  | 1 RED = AMPS 1 WHITE = AMPS 1 BLUE = AMPS 1 RED = AMPS 1 WHITE = AMPS 1 BLUE = AMPS |
| 18. CONFIRM ALARM LEVEL EXTRA HIGH FLOAT TO OPS. CENTRE |  |  |  |  |
| 19. CONFIRM ALARM OVERFLOW TO ENVIROMENT TO OPS. CENTRE |  |  |  |  |
| 20. CONFIRM ALARM TO STORAGE TO OPS CENTRE |  |  |  |  |
| 21. CONFIRM PUMP OVERLOAD PROTECTION TRIPS. TEST BY LOWERING SETTING ON OVERLOAD RELAY |  |  |  |  |
| 22. ALARM LEVEL SWITCH INSTALLED SATISFACTORY |  |  |  |  |
| 1. SITE COMMISSIONING SHEET– MINOR SEWERAGE P/S – ELECTRICAL Page 2 of 2 |
|  | ACC | REJ | N.A | COMMENTS |
| 23. ULTRASONIC PROBE INSTALLED SATISFACTORY (REPORT ) |  |  |  |  |
| 24. LEVEL CONTROLLER PROGRAM SETTINGS AS DRAWING |  |  |  |  |
| 25. ALARM LEVEL SETTINGS AS DRAWING |  |  |  |  |
| 26. AS CONSTRUCTED DRAWINGS MARKED UP (3 SETS ) |  |  |  |  |
| 27. SCADA CONNECTIONS TESTED |  |  |  |  |
| 28. KWH METER NUMBER ( ) |  |  |  |  |
| 29. ACCESS TO ELECTRICAL ITEMS SATISFACTORY |  |  |  |  |
| 30. ALARM LINE PHONE NUMBER (09 ) |  |  |  |  |
| 31. POWER FAILURE ALARM TO OPS. CENTRE |  |  |  |  |
| 32. TEST SECURITY ALARM TO OPS. CENTRE |  |  |  |  |
| 33. LABELLING APPROPRIATE AS PER DS 51 |  |  |  |  |
| 34. CUBICLES AND MOTORS PAINT WORK APPROPRIATE |  |  |  |  |
| 35. DEBRIS REMOVED FROM CUBICLES |  |  |  |  |
| 36. DRAINAGE AROUND TRANSFORMER APPROPRIATE |  |  |  |  |
| 37. UNDERGROUND CABLES LOCATED ON DRAWINGS |  |  |  |  |
| 38. MAGFLOW VERIFICATION TESTED |  |  |  |  |
| 39. INSTRUMENT CALIBRATION SHEETS – ( MAGFLOWS ) |  |  |  |  |
| 40. SYSTEM FUNCTION TEST |  |  |  |  |
| LEDGEND: ACC = Acceptable REJ = Rejected N.A = Not Applicable |  |  |  |  |

2. REMARKS / REMEDIAL ACTIONS

| 3. SIGNOFFS |  |
| --- | --- |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |