| 1. GENERAL DATA |
| --- |
| PROJECT NAME: | PROJECT NO.: |
| WC P.O. / CONTRACT NO.: | LINE / ITEM NO.: |

| 2. GENERAL DATA |
| --- |
| Termination Drawing: | Equipment Layout Drawing: |
| Manufacturer: | Vendor: |
| Rated Output Voltage (V AC/DC): | Rated Load (kW/kVA): |
| Rated Backup Duration (min): | Battery Type: |

| 3. INSPECTION | YES | NO | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- |
| PRE-LOAD TESTING |
| 1 | System is ready to energy are all loads isolated, test load is available |  |  |  |  |
| 2 | Refer to UPS Manual for vendor procedures |  |  |  |  |
| 3 | UPS supply 1 (V): |  |  |  |  |
| 4 | UPS supply 2 (V): |  |  |  |  |
| 5 | UPS supply change over switch operate correctly: |  |  |  |  |
| 6 | UPS output voltage (V): |  |  |  |  |
| 7 | Battery compartment ventilation operating correctly: |  |  |  |  |
| 8 | UPS output voltage: |  |  |  |  |
| 9 | Battery compartment ventilation operating correctly: |  |  |  |  |
| UPS FUNCTION |
| 1 | UPS bypass mode correct |  |  |  |  |
| 2 | UPS diagnostic output – AC fail |  |  |  |  |
| 3 | UPS diagnostic output – UPS on bypass |  |  |  |  |
| 4 | UPS diagnostic output – Battery low |  |  |  |  |
| 5 | UPS diagnostic output – UPS on |  |  |  |  |
| 6 | UPS diagnostic output – UPS fail |  |  |  |  |
| 7 | UPS panel indications operating correctly |  |  |  |  |
| 8 | Allow 24 hours charging before doing load tests |  |  |  |  |

| 4. INSPECTION | YES | NO | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- |
| PREPARATION |
| 1 | UPS has been charged |  |  |  |  |
| 2 | Test load available |  |  |  |  |
| 3 | Expected discharge hours calculated |  |  |  |  |
| POWER LOAD TEST |
| 1 | Measure and record voltages and currents |  |  |  |  |
| 2 | With supply remaining energised, apply load |  |  |  |  |
| 3 | Maintain supply and load for 2-4 hours |  |  |  |  |
| 4 | Record readings at start |  |  |  |  |
| 5 | Record readings at end of period |  |  |  |  |
| 6 | Unit operating correctly |  |  |  |  |
| DISCHARGE TEST |
| 1 | Isolate both supplies to UPS for discharge test |  |  |  |  |
| 2 | Record start time readings |  |  |  |  |
| 3 | Record readings at interval of 20% calculated backup time up to 100% backup time. (Discontinue test if output drop below 80%) |  |  |  |  |
| RECHARGE |
| 1 | After taking readings up to 100% calculated backup time, disconnect load and re-energise UPS supply |  |  |  |  |
| 2 | Record initial recharge readings and determine expected recharge time based on unit ratings |  |  |  |  |
| 3 | After recharge, repeat measurements |  |  |  |  |
| 4 | Check electrolyte level |  |  |  |  |

| 5. CALCULATED DISCHARGE TIME |
| --- |
| Load: Rated A kW | Test Load: Rated A kW |
| Duration: Rated A kW | Expected: Hours (100% discharge time) |

| 6. TEST MEASUREMENTS |
| --- |
|  | Bus Volts | Charge Amps | Output Volts | Output Amps | Time |
| Initial power up |  |  |  |  |  |
| After 24 hours charge |  |  |  |  |  |
| Power Load Test |  |  |  |  |  |
| At start |  |  |  |  |  |
| After 2-4 hrs |  |  |  |  |  |
| Discharge Test |  |  |  |  |  |
| At start |  |  |  |  |  |
| 20% exp duration |  |  |  |  |  |
| 40% exp duration |  |  |  |  |  |
| 60% exp duration |  |  |  |  |  |
| 80% exp duration |  |  |  |  |  |
| 100% exp duration |  |  |  |  |  |
| Recharge |  |  |  |  |  |
| At start |  |  |  |  |  |
| After completed duration |  |  |  |  |  |

| 7. LOAD TESTS | YES | NO | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- |
| 1 | Data Sheet marked up as commissioned |  |  |  |  |
| 2 | Schematic drawing marked up as commissioned |  |  |  |  |
| 3 | Punch list item(s) generated and entered into database |  |  |  |  |

8. REMARKS / REMEDIAL ACTIONS

| 9. SIGNOFFS |  |
| --- | --- |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |