| 1. GENERAL DATA |
| --- |
| PROJECT NAME: | PROJECT NO.: |
| WC P.O. NO.: | LINE NO.: |
| 2. ULTRASONIC FLOW METER DATA |
| MANUFACTURER: |  |
| MODEL NO.: | SERIAL NO.: |
| WC FLOW METER NO.: | WC DWG NO.: |
| 3.1 SENSOR DATA |
| MODEL NO.: | SERIAL NO.: |
| MOUNTING TYPE: | COUPLING TYPE: |
| 3.2 TRANSMITTER DATA |
| MODEL NO.: | SERIAL NO.: |
| RANGE (units): | POWER SUPPLY: |
| 4. INSPECTION | DONE /YES | NO | N/A | COMMENTS/DETAILS |
| 1 | Sensor location meets calming length specification as per manufacturer’s recommendations (ie dependent on upstream and downstream pipe configuration) |  |  |  |  |
| 2 | Sensor type correct for application |  |  |  |  |
| 3 | Sensor mounting correct & secure – no air gaps between sensor and pipe; sensors mounted on the side for horizontal pipes not top or bottom; mounted on vertical pipes such that the direction of flow is upwards |  |  |  |  |
| 4 | Installed distance between sensors is correct as per calculated value |  |  |  | Calculated: Actual: |
| 5 | Location of the transmitter is within cable reach of the sensors |  |  |  |  |
| 6 | Sound path No. of traverses |  |  |  | Result: |
| 7 | Pipe surface preparation acceptable as per manufacturer’s recommendations |  |  |  |  |
| 8 | Sensor coupling material in place & correct |  |  |  |  |
| 9 | Signal cable run installation and protection acceptable |  |  |  |  |
| 10 | Transmitter installation acceptable |  |  |  |  |
| 11 | Sensor cables terminated correctly |  |  |  |  |
| 12 | All connections tight, and correct |  |  |  |  |
| 13 | Transmitter ready for commissioning |  |  |  |  |

| 5. REMARKS / REMEDIAL ACTIONS |
| --- |
| 6. SIGNOFFS |  |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |