A) INTRODUCTION

The following procedure is intended to ensure that the quality of constructed product and its associated activities are completed by competent persons and:

- Comply with current and applicable specified requirements (including Corporation specifications / contract terms and conditions, national / international standards, manufacturer’s recommendations and industry best practices.

- Are conducted in a safe and professional manner.

- Provide an audit trail for verification of Quality Assurance and Quality Control compliance.

This procedure is for all RECIPROCATING COMPRESSORS. Competent personnel shall complete all inspection / construction activities and record all activities on Water Corporation Document ITP-CV-M-COMPRESSORS-RECIPROCATING; for each asset constructed.

NOTE:

- Please ensure that all ITP documents are completed by a competent person and that all Water Corporation SAFETY and operational requirements are to be complied with at all times in relation with Water Corporation and AS/NZS Standards where applicable.

B) COMPLETED DOCUMENTS

Completed documents are to be scanned and saved as a .pdf file in the relevant AQUA folder utilising the following naming convention:

LOCATION - DISCIPLINE - ASSET – ASSET TYPE – VENDOR NAME – DOCUMENT TYPE – P&ID TAG – REVISION NUMBER

E.g. RavenswoodPS_M_Valve_Butterfly_Tyco_CV_1000BV3422_1

The commissioning manager shall coordinate incorporation of completed ITPs in conjunction with the CAMEL.

Feedback on improvements to ITPs should be directed to MESB Mechanical for incorporation into future versions.

* All Construction Verification documents shall contain the following sections (1 – 2) which capture generic asset information

| 1. REFERENCE INFORMATION |
| --- |
| INSPECTION DATA | ASSET DATA |
| PROJECT NAME: | MANUFACTURER: |
| LOCATION: | MF SERIAL NO: |
| INSPECTION DATE: | WC FLER / TAG NO: |
| INSPECTOR NAME: | TYPE / MODEL NO / SIZE: |
| PROJECT / CONTRACT NO: | DESIGN CRITERIA: |
| ATTENDEES: |

| 2. INSPECTION PREPARATION |
| --- |
|  | OSH compliance requirements. |
|  | Obtain QA / QC documentation (review outstanding items). |
|  | Relevant Water Corporation standards. |
|  | Relevant Australian Standards. |
|  | Supporting contract documentation / approved drawings. |
|  | Provision of required test equipment. |
|  | Provision of required test reports. |

*Contents of Section 3 (Inspection) and Section 4 (Test) are Asset Specific and shall reflect relevant SPS / Australian Standard(s) where practicable. Entries shall also be worded to reflect the procedures involved in a step-by-step manner; i.e. “Conduct visual inspection and ensure pre-start photographs are taken”, “Extract bearing housing covers to expose bearings and full shaft length”.

| 3. INSPECTION & 4. TESTING | YES | NO | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- |
| GENERAL |
| 1 | Compressor installed in correct location per drawings? |  |  |  |  |
| 2 | Compressor and motor direction of rotation correct per drawings? |  |  |  | Direction of rotation: ACW CW (as viewed from drive end) |
| 3 | Compressor installed per manufacturer and Water Corporation recommendations? |  |  |  |  |
| 4 | Confirm cautionary labels installed on compressor |  |  |  |  |
| 5 | Integral safety relief valves installed |  |  |  |  |
| SHAFT, BEARINGS AND SEALS |
| 6 | All transportation shaft locking and anti-brinelling devices removed if applicable? |  |  |  |  |
| 7 | Compressor and motor bearings adequately lubricant/greased? |  |  |  | Check lubricant level |
| 8 | Bearing RTDs fitted if applicable? |  |  |  |  |
| 9 | Vibration transducers if applicable fitted? |  |  |  |  |
| 10 | Un-used tappings on housings plugged? |  |  |  |  |
| LEVELLING AND ALIGNMENT OF COMPRESSOR |
| 11 | Plinth surface roughness acceptable? |  |  |  |  |
| 12 | Foundation bolts size, material and grade correct? |  |  |  | Size: _______ Material:______________ Grade: ___________________________ |
| 13 | Gap between baseframe and top of plinth adequate for grouting? Note most compressors are not grouted in place. During major overhaul the entire compressor is sent away or compressor is serviced in-situ. |  |  |  | Gap: ______________ mm |
| 14 | Confirm baseframe forklift recesses are accessible for removal of entire compressor |  |  |  |  |
| 15 | Correct type of grout used for foundation bolts and baseframe? |  |  |  | Bolt grout: ________________________ Baseframe grout:___________________ |
| 16 | Grout flowable, adequately distributed, free of voids and level with top of baseframe? |  |  |  |  |
| 17 | Correct protrusion of foundation bolt threads past nut? |  |  |  |  |
| 18 | Compressor baseframe foundation bolts tightened? |  |  |  |  |
| VENTS, DRAINS, SEAL AND COOLING WATER |
| 19 | Condensate drain piping and valves fitted and routed to floor drain? |  |  |  |  |
| 20 | Baseframe drain connected? |  |  |  |  |
| 21 | For water cooled compressors ensure water piping of correct size with required valves and filters fitted (if applicable) ? |  |  |  |  |
| 22 |  |  |  |  |  |
| 23 | Un-used tappings on compressor casing plugged? |  |  |  |  |
| AIR INTAKE |
| 24 | Ensure air cooling intake louvre has sufficient clearance from building walls and discharge duct to avoid recirculation of hot air that may cause overheating |  |  |  |  |
| 25 | Check air intake filter installed (i.e. Donaldson cyclone filter) especially for dusty outside installations |  |  |  |  |
| 26 | Confirm any ductwork is fully self-supporting |  |  |  |  |
| 27 | Check bolt size, material and grade correct on ductwork ? |  |  |  | Size: _______ Material:_____________ Grade: 4.6 8.8 Other_________ |
| 28 | Correct protrusion of bolt threads past nut? |  |  |  |  |
| 29 | Correct bolt tightening sequence followed? |  |  |  |  |
| 30 | Final bolt torques correct? |  |  |  | Torque: __________________ Nm Refer to compressor manufacturer’s recommendation. |
| DISCHARGE COMPRESSED AIR PIPEWORK |
| 31 | Discharge pipework correctly supported with zero load on compressor nozzle? |  |  |  |  |
| 32 | Mating threaded connections or flanges flat, clean and free of irregularities? |  |  |  |  |
| 33 | Gasket material and thickness correct for flanged pipework? |  |  |  | Material: CMF EPDM Other______ Thickness: ____________ mm |
| 34 | Bolt size, material and grade correct for flanged pipework? |  |  |  | Size: _______ Material:_____________ Grade: 4.6 8.8 Other_________ |
| 35 | Correct protrusion of bolt threads past nut? |  |  |  |  |
| 36 | Correct bolt tightening sequence followed? |  |  |  |  |
| 37 | Final bolt torques correct? |  |  |  | Torque: __________________ Nm Refer to compressor manufacturers recommendation. |
| 38 | Confirm refrigerated drier downstream of compressor has been installed to manufacturer’s recommendations to drop out any entrained moisture (if applicable) |  |  |  |  |
| 39 | Confirm oil separator has been installed to remove carryover oil from compression |  |  |  |  |
| GUARDING AND ENCLOSURE PANELLING |
| 40 | Fan guard(s) fitted on any exposed rotating parts and secure? |  |  |  | Most compressors are fully enclosed and access to components requires removal of panels after compressor is isolated |
| 41 | Ensure removable panels can provide full access to equipment requiring maintenance |  |  |  |  |

*Contents of Section 5 to be retained where applicable; i.e. if coatings inspection is required. Sections 6 & 7 to be retained in all ITPs.

| 5. COATINGS INSPECTION | YES | NO | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- |
| 1 | Check that asset external coating is free of damage |  |  |  | Repair if required according to coating manufacturers recommendation |

| 6. REMARKS / REMEDIAL / FOLLOW UP ACTIONS | ACTION BY | TARGET DATE | STATUS |
| --- | --- | --- | --- |

| 7. SIGNOFFS |
| --- |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |