- All ITR documents to be completed & witnessed by competent person/s

- Compliance to be achieved to contract requirements and all latest versions of applicable standards

| 1. REFERENCE INFORMATION |
| --- |
| INSPECTION DATA | ASSET DATA |
| PROJECT NAME: | MANUFACTURER: |
| LOCATION: | MF SERIAL NO: |
| INSPECTION DATE: | WC FLER / TAG NO: |
| INSPECTOR NAME: | TYPE / MODEL NO / SIZE: |
| PROJECT / CONTRACT NO: | DESIGN CRITERIA: |
| ATTENDEES: |

| 2. INSPECTION PREPARATION |
| --- |
|  | OSH compliance requirements. |
|  | Obtain QA / QC documentation (review outstanding items). |
|  | Relevant Water Corporation standards. |
|  | Relevant Australian Standards. |
|  | Supporting contract documentation / approved drawings. |
|  | Provision of required test equipment. |
|  | Provision of required test reports and certificates; i.e. hydrostatic test, material certificates, etc. |

| 3. INSPECTION | YES | NO | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- |
| GENERAL |
| 1 | Locate and verify that name plate/label details match specification or drawings |  |  |  | Check the following Flow rate ACFM/ Motor HP /TagNumber/ /Design Pressure |
| 2 | Confirm if O&M Manuals have been provided (hardcopy / softcopy) |  |  |  | Hardcopy / softcopy? (please circle) |
| MATERIALS AND ARRANGEMENT |
| 3 | Verify construction materials with specification and relevant drawings |  |  |  |  |
| 4 | Confirm overall dimensions and mounting details are correct |  |  |  | Checked against: MF Dimensions / G.A. Dwg |
| 5 | Confirm outlet pipework connection details match specifications or drawings |  |  |  | Connection Aust/International Standard: Connection Type: Connection Size: Connection Class: |
| 6 | Confirm guards & sound enclosure/hood installed |  |  |  |  |
| 7 | Air inlet dust filter to 0.01 microns |  |  |  |  |
| 8 | Oil free or outlet filter for removal of oil content to 0.01 parts per million |  |  |  |  |
| 9 | Confirm mounting on fabricated baseplate |  |  |  |  |
| 10 | Confirm automatic condensate drain installed |  |  |  |  |
| 11 | Confirm inter-stage cooling, pressure gauges and relief valves are installed |  |  |  |  |
| 12 | Confirm after-stage cooling and relief valves are installed |  |  |  |  |
| 13 | Confirm an un-loader is installed to prevent starting against full load |  |  |  |  |
| 14 | Confirm a close coupled 415 V AC electric motor is installed |  |  |  |  |
| 15 | Confirm low oil level switch is installed |  |  |  |  |
| 16 | Confirm self contained DOL starter with local controls is installed |  |  |  |  |
| 17 | Confirm Local – Off – Remote selector switch is installed |  |  |  |  |
| 18 | Confirm Start and stop pushbuttons are installed |  |  |  |  |
| 19 | Confirm voltage-free normally open contacts wired to terminals to allow remote monitoring of the Remote position of the selector switch is installed |  |  |  |  |
| 20 | Confirm a 24 V DC control interposing relay wired to terminals to interface with the Principal’s control system when selected for remote control is installed |  |  |  |  |

| 4. TEST | PASS | FAIL | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- |
| 1 | Factory Acceptance Tests accepted and attached |  |  |  |  |
| 2 | Test Certificates (if applicable) accepted and attached |  |  |  |  |
| 3 | Load Bank Tests accepted and attached |  |  |  |  |
| 4 | Confirm belt tension is correct if applicable (refer to manual) |  |  |  |  |

*Contents of Section 5 to be retained where applicable; i.e. if coatings inspection is required. Sections 6-9 to be retained in all ITPs.

| 5. COATINGS INSPECTION | YES | NO | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- |
| 1 | Verified construction materials with specification and relevant drawings |  |  |  | Substrate material: |
| 2 | Review surface pre-treatment and/or preparation procedure (circle A1: Surface preparation of Steel/Cast Iron or state Other) |  |  |  | A1 / OTHER _________________ |
| 3 | Verify coating system and specification ensuring that product is approved for purpose |  |  |  |  |
| 4 | Ensure that surface preparation was acceptable and free from contaminants prior to coating/complies to spec Consider dust and spent abrasive, oil and contamination, flash rusting, slag, porosity, weld spatter, sharp edges, free from laminations, free from burrs etc |  |  |  | Class of surface finish (if known): Profile (if known): Coating application (if known): |
| 5 | Consider if conditions acceptable for testing. Surface temperature should be least 3ºC above dew point and relative humidity less than 85 % before testing |  |  |  | Conditions: |
| 6 | Fully cured coating system should be adherent while in their service condition (Method AS/NZS 3894.9) |  |  |  | Failure force (if known): |
| 7 | Assess degree of cure and hardness of coating is acceptable (method AS 3894.4). Allow sufficient drying and curing of the coating prior conducting testing. The length of time shall be obtained from the coating manufacture. |  |  |  | Method used: |
| 8 | Checked that flange faces are clean and are free from any defects resulting from corrosion or any other cause |  |  |  |  |
| 9 | Visually inspect surfaces and ensure is adequately clean and dry prior to testing |  |  |  | Method/chemicals used: |
| 10 | Check internal coating type and verify in accordance with relevant specification (circle C1:Zinc Rich Epoxy Coating on Steel/Cast Iron or state, |  |  |  | C1 / / OTHER _____________ |
| 11 | Visually inspect condition of internal coating appearance including uniformity, colour and free from any defect that could impair performance and/or appearance of coating. |  |  |  |  |
| 12 | Check external coating type and verify in accordance with relevant specification (circle : Epoxy Coating on Steel/Cast Iron or state, : Protective Coating on Steel/Cast Iron or state Other ) |  |  |  | C1 / / OTHER _____________ |
| 13 | Visually inspect condition of external coating appearance including uniformity, colour and free from any defect that could impair performance and/or appearance of coating. |  |  |  |  |
| 14 | Calibrate thickness tester to standard of uniform and calibrated thickness, covering appropriate range of film thicknesses to be measured |  |  |  | Method/instrument used: |
| 15 | Visually inspect and measure dry film thickness (DFT) in at least 10 locations on coated surfaces. Record values, ensure compliance with spec and record in table below (note that Flange Thickness is not considered acceptable if not within minimum – maximum range) |
| 16 | Ensure coating fully cured prior continuity testing by checking datasheet for required time to full cure or other appropriate test method |  |  |  | Temp/time: Test method: |
| 17 | Calibrate holiday detector (spark tester) electrode with appropriate volt meter which has been laboratory calibrated within the last 2 years to proposed voltage. Record brand and model of spark tester to be used. |  |  |  | Brand/model used: |
| 18 | Carry out spark test on internal coating in accordance to AS/NZS 3894.1 Continuity testing of non-conductive coating – High Voltage (brush) method. Specify voltage at which test is carried out. |  |  |  | Test Voltage: V |
| 19 | Carry out spark test on external coating accordance to AS/NZS 3894.1 Continuity testing of non-conductive coating – High Voltage (brush) method. Specify voltage at which test is carried out. |  |  |  | Test Voltage: V |
| 20 | Valve passes continuity testing with zero defects (including pinholes, holidays, cracks and other discontinuities) detected in finished coating for immersed/buried conditions and/or subsequent repairs have been carried out before being placed in service. |  |  |  |  |

| Coating Thickness: | Internal (micrometers): | External (micrometers): | Flange (micrometers ): |  |
| --- | --- | --- | --- | --- |
| Specified min |  |  |  |  |
| Specified max |  |  |  |  |
| Measured 1 |  |  |  |  |
| Measured 2 |  |  |  |  |
| Measured 3 |  |  |  |  |
| Measured 4 |  |  |  |  |
| Measured 5 |  |  |  |  |
| Measured 6 |  |  |  |  |
| Measured 7 |  |  |  |  |
| Measured 8 |  |  |  |  |
| Measured 9 |  |  |  |  |
| Measured 10 |  |  |  |  |
| Average |  |  |  |  |
| Complies with Spec | YN | YN | YN |  |
| Note any comment or variation to test procedure that will assist in interpretation of results: |

Refer to AS/NZS 1627 series for Metal Finishing – Preparation and Pre-treatment of Surfaces

2 Refer to AS/NZS 3894.7 for practical procedure for Determination of Surface Temperature of metal surfaced (pre-coating)

3 Refer to AS/NZS 3894.3 methods for Determination of Dry Film Thickness

4 Method AS 3894.3 refers Determination of Dry Film Thickness

| 6. REMARKS / REMEDIAL / FOLLOW UP ACTIONS | ACTION BY | TARGET DATE | STATUS |
| --- | --- | --- | --- |

| 7. SIGNOFFS |
| --- |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |

POST TRANSPORTATION INSPECTION

- Inspection to be completed at point of delivery

- If a supply verification was not completed at the manufacturer, both supply verification and post transportation inspection should be completed at point of delivery.

| 8. POST TRANSPORTATION REMARKS / REMEDIAL / FOLLOW UP ACTIONS | ACTION BY | TARGET DATE |
| --- | --- | --- |

| 9. SIGNOFFS |
| --- |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |

# Footnotes

Refer to AS/NZS 1627 series for Metal Finishing – Preparation and Pre-treatment of Surfaces

Refer to AS/NZS 3894.7 for practical procedure for Determination of Surface Temperature of metal surfaced (pre-coating)

Refer to AS/NZS 3894.3 methods for Determination of Dry Film Thickness

Method AS 3894.3 refers Determination of Dry Film Thickness