| All ITR documents to be completed & witnessed by competent person/s Compliance to be achieved to contract requirements and all latest versions of applicable standards |
| --- |
| 1. REFERENCE INFORMATION |
| INSPECTION DATA | ASSET DATA |
| PROJECT NAME: | MANUFACTURER: |
| LOCATION: | INSPECTION DATE |
| INSPECTOR NAME: |  |
| PROJECT / CONTRACT NO: | DESIGN CRITERIA: |
| ATTENDEES: |

| 2. INSPECTION PREPARATION |
| --- |
|  | OSH compliance requirements. |
|  | Obtain QA / QC documentation (review outstanding items). |
|  | Relevant Water Corporation standards. |
|  | Relevant Australian Standards. |
|  | Supporting contract documentation / approved drawings. |
|  | Provision of required test equipment. |
|  | Provision of required test reports. |

*Contents of Section 3 (Inspection) and Section 4 (Test) are Asset Specific and shall reflect relevant SPS / Australian Standard(s) where practicable. Entries shall also be worded to reflect the procedures involved in a step-by-step manner; i.e. “Conduct visual inspection and ensure pre-start photographs are taken”, “Extract bearing housing covers to expose bearings and full shaft length”.

| 3. INSPECTION & 4. TESTING | YES | NO | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- |
| GENERAL |
| 1 | Fan installed in correct location and orientation as per drawings? |  |  |  |  |
| 2 | Fan and motor direction of rotation correct per drawings? |  |  |  | Direction of rotation: ACW CW (as viewed from drive end) |
| 3 | Fan installed per manufacturer and Water Corporation recommendations? |  |  |  |  |
| SHAFT, BEARINGS AND SEALS |
| 4 | All shaft locking and anti-brinelling devices removed? |  |  |  |  |
| 5 | Fan and motor bearings adequately greased? |  |  |  | Note removal of the bearing housing cover maybe required |
| 6 | Bearing end float within tolerance? |  |  |  | Fan bearing float: _____________ mm Motor bearing float: ___________ mm |
| 7 | Bearing RTDs fitted? |  |  |  |  |
| 8 | Vibration transducers fitted? |  |  |  |  |
| LEVELLING AND ALIGNMENT OF FAN MOTOR ASSEMBLY |
| 9 | Support steelwork clean and level ? |  |  |  |  |
| 10 | Fastener size, material and grade correct as per drawings? |  |  |  | Size: _______ Material:______________ Grade: ___________________________ |
| 11 | Fasteners accessible for future disassembly? |  |  |  | Gap: ______________ mm |
|  | Fan and motor plumb and level? |  |  |  |  |
| 12 | - Horizontal (eg. fan shafts?) |  |  |  |  |
| 13 | - Vertical (eg. Fan flange faces) |  |  |  |  |
| 14 | Fan and ductwork/flexible joint flanges aligned and parallel? |  |  |  |  |
| 15 | Correct protrusion of fastening bolt threads past nut? |  |  |  |  |
| 16 | Fastening bolts tightened? |  |  |  |  |
| 17 | Final alignment acceptable? |  |  |  | Flexible joints should be aligned to fan flange faces |
| 18 | Fan to baseframe bolts tightened? |  |  |  |  |
| 19 | Motor to baseframe bolts tightened? |  |  |  |  |
| 20 | Vibrations dampeners installed, secure and compressed with preload |  |  |  | Vibration dampeners should not be fully compressed when fan is not running |
| INLET FLANGE BOLT-UP |
| 21 | Inlet ducting correctly supported with zero load on fan inlet flange? |  |  |  |  |
| 22 | Mating flanges flat, clean and free of irregularities? |  |  |  |  |
| 23 | Gasket material and thickness correct? |  |  |  |  |
| 24 | Bolt size, material and grade correct? |  |  |  | Size: _______ Material:_____________ Grade: 4.6 8.8 Other_________ |
| 25 | Correct protrusion of bolt threads past nut? |  |  |  |  |
| 26 | Correct bolt tightening sequence followed? |  |  |  |  |
| 27 | Final bolt torques correct? |  |  |  | Torque: __________________ Nm Refer to fan manufacturer’s recommendation. |
| OUTLET FLANGE BOLT-UP |
| 28 | Discharge ducting correctly supported with zero load on fan outlet flange? |  |  |  |  |
| 29 | Mating flanges flat, clean and free of irregularities? |  |  |  |  |
| 41 | Gasket material and thickness correct? |  |  |  |  |
| 42 | Bolt size, material and grade correct? |  |  |  | Size: _______ Material:_____________ Grade: 4.6 8.8 Other_________ |
| 43 | Correct protrusion of bolt threads past nut? |  |  |  |  |
| 44 | Correct bolt tightening sequence followed? |  |  |  |  |
| 45 | Final bolt torques correct? |  |  |  | Torque: __________________ Nm Refer to fan manufacturers recommendation. |
| COUPLING AND GUARD |
| 46 | Coupling bolts correct size, material and grade (if not supplied by coupling manufacturer)? |  |  |  | Size: _______ Material: ____________ Grade: __________________________ |
| 47 | Final coupling bolts tightened? |  |  |  | Torque: _____________________ Nm Refer to coupling manufacturer’s recommendation. |
| 48 | Guard(s) fitted and secure? |  |  |  |  |
| 49 | Coupling/shaft rotates relatively freely? |  |  |  |  |

*Contents of Section 5 to be retained where applicable; i.e. if coatings inspection is required. Sections 6 & 7 to be retained in all ITRs.

| 5. COATINGS INSPECTION | YES | NO | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- |
| 1 | Check that asset external coating is free of damage |  |  |  | Repair if required according to coating manufacturers recommendation |

| 6. REMARKS / REMEDIAL / FOLLOW UP ACTIONS | ACTION BY | TARGET DATE | STATUS |
| --- | --- | --- | --- |

| 7. SIGNOFFS |
| --- |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |