| All ITR documents to be completed & witnessed by competent person/s Compliance to be achieved to contract requirements and all latest versions of applicable standards |
| --- |
| 1. REFERENCE INFORMATION |
| INSPECTION DATA | ASSET DATA |
| PROJECT NAME: | MANUFACTURER: |
| LOCATION: | INSPECTION DATE |
| INSPECTOR NAME: |  |
| PROJECT / CONTRACT NO: | DESIGN CRITERIA: |
| ATTENDEES: |

| 2. INSPECTION PREPARATION |
| --- |
|  | OSH compliance requirements. |
|  | Obtain QA / QC documentation (review outstanding items). |
|  | Relevant Water Corporation standards. |
|  | Relevant Australian Standards. |
|  | Supporting contract documentation / approved drawings. |
|  | Provision of required test equipment. |
|  | Provision of required test reports. |

*Contents of Section 3 (Inspection) and Section 4 (Test) are Asset Specific and shall reflect relevant SPS / Australian Standard(s) where practicable. Entries shall also be worded to reflect the procedures involved in a step-by-step manner; i.e. “Conduct visual inspection and ensure pre-start photographs are taken”, “Extract bearing housing covers to expose bearings and full shaft length”.

| 3. INSPECTION & 4. TESTING | YES | NO | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- |
| GENERAL |
| 1 | Pump installed in correct location per drawings? |  |  |  |  |
| 2 | Pump and motor direction of rotation correct per drawings? |  |  |  | Direction of rotation: ACW CW (as viewed from drive end) |
| 3 | Pump installed per manufacturer and Water Corporation recommendations? |  |  |  |  |
| COLUMN-LESS PUMPS HANGER TYPE |
| 4 | Ensure stainless steel hanger pipe/rod is securely fastened to pump during install |  |  |  |  |
| 5 | Ensure stainless steel hanger pipe/rod is securely connected to the bore head casing cover at the surface |  |  |  |  |
| 6 | Confirm stainless steel inflatable packer assembly is fitted to the pump discharge outlet to seal pump to the bore casing e.g. Age Developments or equivalent |  |  |  |  |
| 7 | Ensure tubing and fittings to inflate and deflate the packer is secured to the hanger pipe and extend to the surface |  |  |  |  |
| 8 | Confirm electric drop cable is taped to the hanger pipe |  |  |  |  |
| 9 | For bores with significant deviation, confirm packer assembly has been fitted with centralisers |  |  |  |  |
| 10 | Ensure pumpset motors are fitted with bore centralizers to prevent contact with production casing which can cause hotspots and premature motor failure |  |  |  |  |
| COLUMN PUMPS (RIGID COLUMN) |
| 11 | Ensure the correct column type has been used for the application as per drawings and specifications |  |  |  |  |
| 12 | Confirm rigid column is of FRP/GRP twist and lock type e.g. Permaglass with Kwik Lok |  |  |  |  |
| 13 | Confirm the electric drop cable, ground water level monitoring ducts and bubbler tube has been taped to the column |  |  |  | Strapping tape shall be Advance AT10 PVC Heavy Duty Pipe wrap Tape 48mmx33m or equivalent |
| 14 | Ensure the bubbler tube and level transmitter is located at commencement of the column i.e. immediately above pump non-return valve |  |  |  | Bubbler tubing shall be ¼” SMC black low density polyethylene tubing TE1400 in 100m coils or equivalent |
| 15 | Ensure bubbler tube end is cut at an angle e.g. 45 degrees |  |  |  |  |
| COLUMN PUMPS (FLEXIBLE COLUMN) |
| 16 | Confirm flexible column is “Wellmaster” or equivalent |  |  |  |  |
| 17 | Ensure a break-off plug system (internally at bottom of column) has been fitted to allow column drainage to facilitate pumpset retrieval |  |  |  | Ensure a hole is not drilled in pump NRV in-lieu of break-off plug |
| 18 | Confirm electric drop cable, groundwater level monitoring ducts, bubbler tube are secured to column using cable straps |  |  |  |  |
| 19 | Confirm bubbler tube is taped to stainless steel fitting at commencement of column and fed through cable straps to surface |  |  |  |  |
| 20 | Ensure bubbler tube end is cut at an angle e.g. 45 degrees |  |  |  |  |
| LINESHAFT PUMPS (DIESEL ENGINE OR MOTOR DRIVEN) |
|  | General |  |  |  |  |
| 21 | Confirm an appropriate poppet type resilient seated foot valve has been installed on pump inlet suitable |  |  |  | The foot valve maintains full discharge column of water during stoppage so lineshaft bearings are immersed and lubricated. For possible high hammer situations the valve may need to be spring loaded |
| 22 | Confirm a grade 316 stainless steel conical strainer is fitted on strainer inlet |  |  |  |  |
| 23 | Ensure discharge column is made of heavy duty carbon steel pipe sections with precision machined threads at each end |  |  |  |  |
| 24 | Confirm each column section is fitted with a coupling machined from ductile iron or heavy duty seamless steel tubing |  |  |  |  |
| 25 | Check bearing housings are manufactured from bronze listed in SPS 507 |  |  |  |  |
| 26 | Ensure bearing is retained in housing using either stainless steel circlip or retaining nut |  |  |  |  |
| 27 | Confirm bearings are water lubricated removable elastomeric type for vibration free radial support |  |  |  |  |
| 28 | Check the lineshaft is manufactured from ASTM A276 grade 431 0r 316 with precision machined threads |  |  |  |  |
| 29 | Confirm lineshaft couplings are made of stainless steel of a minimum PREN of 22 and hardness difference at least 50 BHW to that of the shaft |  |  |  |  |
| 30 | Ensure bubbler tube sensor end is taped to commencement of column immediately above pump using strapping tape |  |  |  | Note dip tape and level transmitter normally cannot be used as there is no provision within discharge head |
|  | Discharge Head and Right Angle (RA) Gearbox |  |  |  |  |
| 31 | Concrete apron surface roughness acceptable? |  |  |  |  |
| 32 | Foundation/holding bolts size, material and grade correct? |  |  |  | Size: _______ Material:______________ Grade: ______________ |
| 33 | Gap between discharge head or baseplate and top of plinth adequate for grouting? |  |  |  | Gap: ______________ mm |
| 34 | Check whether a elastomeric gasket is required between grout and discharge head or baseplate for ease of removal |  |  |  |  |
| 35 | Confirm discharge head underside has machined bottom face |  |  |  |  |
| 36 | Confirm discharge head has machined internal screwing to accommodate top discharge column |  |  |  |  |
| 37 | Discharge head, RA gearbox and motor/engine plumb and level? |  |  |  |  |
| 38 | Discharge head flanges aligned and parallel? |  |  |  |  |
| 39 | Discharge flanges comply with AS 4087 |  |  |  | PCD:_____________mm Bolt hole size :______mm No. of bolt holes:_____ |
| 40 | Correct type of grout used for foundation bolts and baseplate? |  |  |  | Bolt grout: ________________________ Baseplate grout:____________ |
| 41 | Grout flowable, adequately distributed, free of voids and level with top of baseplate? |  |  |  |  |
| 42 | Correct protrusion of foundation bolt threads past nut? |  |  |  |  |
| 43 | Foundation bolts tightened? |  |  |  |  |
| 44 | For discharge head fitted with packed seals ensure gland follower bolts snugged up evenly? |  |  |  | Do not overly tighten gland follower as this may lead scoring of shaft sleeve and premature seal failure |
| 45 | Discharge head and motor/engine mounting bolts to baseplate securely fastened to correct torques? |  |  |  |  |
| 46 | Confirm water level bubbler tube connector on discharge head was ‘Swagelok’ fitted |  |  |  |  |
| 47 | Confirm vent and strainer fitted on discharge head |  |  |  |  |
| 48 | Ensure right angle gearbox lubrication is adequate |  |  |  |  |
| 49 | Confirm motor/engine has been installed according manufacturers recommendations |  |  |  |  |
|  | Engine to Gearbox Transmission & Driver |  |  |  |  |
| 50 | Final “cold” alignment between right angle gearbox and motor/engine acceptable? |  |  |  | Attach alignment results to this sheet. Compare results against pump and coupling manufacturer’s tolerances. |
| 51 | Clutch has been installed for large diesel engine to allow uncoupled engine warm-up and cooling down periods? |  |  |  |  |
| 52 | Safety guards painted in safety yellow installed |  |  |  |  |
| 53 | For diesel engine driver has bunded fuel tank |  |  |  |  |
| BORE HEAD AIR RELEASE AND VACUUM BREAK AND COLLECTOR MAIN AIR RELEASE |  |  |  |  |
| 54 | For both column and column-less type pump ensure a bore head ‘air release only” air valve and separate small vacuum breaker “snifter valve” is fitted |  |  |  | Air release valve Size:_____ Model:_________ Vacuum break valve Size:_____ Model:___________ |
| 55 | Ensure collector main air valve downstream of surface non return valve has been installed |  |  |  | Air release valve Size:_____ Model:_________ |
| CONDITION AND WATER LEVEL MONITORING REQUIREMENTS |
| 56 | Confirm whether an integrated monitoring system has been specified and installed e.g. Phoenix/ CTS system |  |  |  | Refer to Table 2.1 of DS 32-01 for summary of condition monitoring and water level monitoring requirements based on bore pump type basis |
| 57 | Confirm a duct for installing and lowering of dip tape (column type only) |  |  |  |  |
| 58 | Confirm whether a bubbler (air line) level monitor has been installed (column type only) |  |  |  |  |
| 59 | Confirm whether a duct for level transmitter (LT) has been installed (column type only) |  |  |  |  |
| 60 | Check whether surface magnetic flowmeter has been installed as per drawing/specifications |  |  |  |  |
| 61 | Confirm a resistance temperature detector (RTD) has been mounted on the pump and motor to detect temperature on bearings and windings and readings available |  |  |  |  |
| 62 | Confirm whether a pressure transmitter has been installed on bore head or collector mains |  |  |  |  |
| 63 | Confirm whether a conductivity meter has been installed |  |  |  |  |
| 64 | Confirm whether a water sampling point has been installed in the bore head or collector mains |  |  |  |  |
| 65 | For column-less pump confirm whether a packer low pressure switch has been installed |  |  |  |  |
| FLOOD PRONE BORE SITE SPECIFIC REQUIREMENTS |
| 66 | Confirm whether a purpose designed elevated earth pad or a steel platform to accommodate headworks pipework above flood level or river bed |  |  |  |  |
| 67 | In-lieu of earth pad or steel platform, has an IP68 glanded bore head casing cover been installed |  |  |  |  |
| CONTAMINATION ENTRY POINTS |
| 68 | Check sealing of concrete slab to production casing |  |  |  |  |
| 69 | Check sealing of bore head cover to concrete apron |  |  |  |  |
| 70 | Check sealing at electrical and instrument cable, sampling and monitoring entry points in bore head cover |  |  |  |  |
| 71 | Confirm correct bunding between diesel engine (if applicable) and bore head |  |  |  |  |
| MOTOR SHROUD |
| 72 | Ensure motor shroud has been installed when velocity of water past motor is less than manufacturers cooling requirements |  |  |  |  |
| PUMP SETTING LEVEL |
| 73 | Ensure pump setting is at least 5m below long term drawdown level or water pumping level (WPL) where practical |  |  |  |  |

*Contents of Section 5 to be retained where applicable; i.e. if coatings inspection is required. Sections 6 & 7 to be retained in all ITRs.

| 5. COATINGS INSPECTION | YES | NO | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- |
| 1 | Check that asset internal coating is free of damage. Areas of focus include suction and discharge nozzle inside corner and tapping locations |  |  |  | Repair if required according to coating manufacturers recommendation |
| 2 | Check that asset external coating is free of damage |  |  |  | Repair if required according to coating manufacturers recommendation |

| 6. REMARKS / REMEDIAL / FOLLOW UP ACTIONS | ACTION BY | TARGET DATE | STATUS |
| --- | --- | --- | --- |

| 7. SIGNOFFS |
| --- |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |