| All ITR documents to be completed & witnessed by competent person/s Compliance to be achieved to contract requirements and all latest versions of applicable standards |
| --- |
| 1. REFERENCE INFORMATION |
| INSPECTION DATA | ASSET DATA |
| PROJECT NAME: | MANUFACTURER: |
| LOCATION: | INSPECTION DATE |
| INSPECTOR NAME: |  |
| PROJECT / CONTRACT NO: | DESIGN CRITERIA: |
| ATTENDEES: |

| 2. INSPECTION PREPARATION |
| --- |
|  | OSH compliance requirements. |
|  | Obtain QA / QC documentation (review outstanding items). |
|  | Relevant Water Corporation standards. |
|  | Relevant Australian Standards. |
|  | Supporting contract documentation / approved drawings. |
|  | Provision of required test equipment (portable vibration monitor and temperature sensor). |
|  | Provision of required test reports and certificates |
|  | Provision of completed construction verification |

| 3. INSPECTION PRELIMINARIES | YES | NO | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- |
| 1 | “Punchlist” reviewed and free of significant defects preventing asset pre-commissioning? |  |  |  |  |
| 2 | Hazard identification and risk assessment for asset pre-commissioning complete? |  |  |  |  |
| 3 | Electrical construction and pre-commissioning ITRs complete? |  |  |  |  |
| 4 | Mechanical and electrical site specific pre-requisite ITRs complete? |  |  |  |  |

*Contents of Section 4 (Inspection) and Section 5 (Test) are Asset Specific and shall reflect relevant SPS / Australian Standard(s) where practicable. Entries shall also be worded to reflect the procedures involved in a step-by-step manner; i.e. “Conduct visual inspection and ensure pre-start photographs are taken”, “Extract bearing housing covers to expose bearings and full shaft length”.

| 4. INSPECTION | YES | NO | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- |
| ROTATION |
| 1 | For lineshaft motor or engine driven pumps check right angle gearbox and motor/engine shafts rotate freely by hand without rub, noise or obvious out of balance? |  |  |  |  |
| CONDITION AND WATER LEVEL MONITORING SYSTEMS |
| 2 | All condition and water level monitoring systems available and on-line? (eg. Integrated system, level transmitter, surface flow meter, pressure transmitter, conductivity meter, low pressure packer switch, RTD on bearings and windings ) |  |  |  |  |
| 3 | Temporary instruments (if required) installed? |  |  |  |  |
| CONTROL AND PROTECTION SYSTEMS |
| 4 | All electrical / instrument control and protection systems available and on-line? (eg. pump and motor protection, process control systems) |  |  |  |  |
| 5 | All mechanical / hydraulic control and protection devices available and on-line? (eg. air and vacuum release valves, non-return valves ) |  |  |  |  |
| HYDRAULICS |
| 6 | Water resting level (WRL) sufficient above suction of bore pump? |  |  |  |  |
| 7 | Discharge column above foot valve primed full of water on column pump? |  |  |  |  |
| 8 | All isolation valves to air and vacuum release valves or pressure gauges on headworks and collector main open? |  |  |  |  |
| 9 | Open flow path available for pumped liquid once the discharge valve is opened? |  |  |  |  |
| 10 | Ensure sampling point valves are isolated. |  |  |  |  |
| 11 | Instrument impulse lines primed and vented? |  |  |  |  |
| 12 | All connections along flow path hydraulically tight (no leaks)? |  |  |  |  |
| 13 | System static head conditions suitable for pump operation? |  |  |  |  |
| ACCESS |
| 14 | Area around bore headworks clean, free of debris and barricaded off from other works (if required)? |  |  |  |  |
| 15 | Emergency stop pushbutton accessible? |  |  |  |  |

| 5. TEST | YES | NO | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- |
| PRESSURE TEST |
| 1 | With the isolation discharge valve closed on the headworks/collector main pressure test to the maximum line pressure. Check for leaks on headworks and collector main, discharge column (column and lineshaft pumps) or bore casing (column-less pump). |  |  |  | Leaks on discharge column or bore casing will obviously not be visible. |
| PERFORMANCE DATA |
| 2 | “Bump” start the pump motor to ensure direction of rotation of motor is correct |  |  |  |  |
| 3 | Water temperature, bearing and winding temperatures and water resting level recorded prior to pump start-up? |  |  |  | Record pre-start measurements per Appendix B. |
| 4 | Pumpset performance parameters recorded during pumpset operation? |  |  |  | Record operating measurements per Appendix B. |
| PERFORMANCE ASSESSMENT |
| 5 | Bearing and winding temperatures acceptable from RTD readings? |  |  |  |  |
| 6 | Bearing vibration levels acceptable ? (if applicable on integrated monitoring system ) |  |  |  |  |
| 7 | For lineshaft pumps pitch and level of noise emanating from right angle gearbox, motor or engine acceptable? |  |  |  |  |
| 8 | Bore Headworks and collector main pipework connections hydraulically tight (no leaks)? |  |  |  |  |
| 9 | Water pumping level (WPL) sufficiently above pump setting? |  |  |  |  |
| 10 | Drawdown acceptable based level transmitter ? |  |  |  |  |
| 11 | Check for signs of surging or hammer in surface pipework |  |  |  |  |
| 12 | On pump shutdown check for return in water level from WPL to WRL |  |  |  |  |
| POST TEST CHECKS |
| 13 | Baseplate welds intact on drivehead (no obvious cracking)? |  |  |  |  |
| 14 | All bolted connections tight for lineshaft drivehead baseplate? |  |  |  |  |
| 15 | All bolted and threaded connections on headworks securely fastened |  |  |  |  |
| 16 | Confirm leak free on headworks and collector main |  |  |  |  |
| 17 | Confirm condition and water level monitoring readings return to expected values |  |  |  |  |

Sections 6 & 7 to be retained in all ITRs.

| 6. REMARKS / REMEDIAL / FOLLOW UP ACTIONS | ACTION BY | TARGET DATE | STATUS |
| --- | --- | --- | --- |

| 7. SIGNOFFS |
| --- |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |

APPENDIX A – SITE SPECIFIC PRE-REQUISITES

| A1. MECHANICAL PRE-REQUISITES | DONE | NO | ITR / DOCUMENT REF. |
| --- | --- | --- | --- |
|  |  |  |  | ITR-SV-M-BORE PUMP |
|  |  |  |  | ITR-CV-M-BORE PUMP |

APPENDIX A – SITE SPECIFIC PRE-REQUISITES (cont’d)

| A2. ELECTRICAL PRE-REQUISITES | DONE | NO | ITR / DOCUMENT REF. |
| --- | --- | --- | --- |

APPENDIX B – PUMP PERFORMANCE RECORD SHEET

| # | PARAMETER | UNITS | MAX. LIMIT (Note 1) | PRE START-UP | T0 (Note 2) | T1 | T2 | T3 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| GENERAL |
| 1 | Time | Hrs:Min |  |  |  | +5 min | +10 min | +15 min |
| 2 | Initial Water Temperature | °C |  |  |  |  |  |  |
| 3 | Atmospheric Pressure | Pa |  |  |  |  |  |  |
| 4 | Pipe Inside Diameters | mm |  |  |  |  |  |  |
| 5 | Electrical String Efficiency (TX,VSD,motor) | % |  |  |  |  |  |  |
| 6 | Pump setting level | m |  |  |  |  |  |  |
| PUMP |
| 7 | Water Resting Level | M |  |  |  |  |  |  |
| 8 | Water Pumping Level | m |  |  |  |  |  |  |
| 9 | Discharge Pressure | Pa |  |  |  |  |  |  |
| 10 | Discharge Head | m |  |  |  |  |  |  |
| 11 | Calculated Pump Head (Refer to Appendix C) | m |  |  |  |  |  |  |
| 12 | Flowrate | m3/hr |  |  |  |  |  |  |
| 13 | Drawdown (WRL-WPL) | m |  |  |  |  |  |  |
| 14 | Discharge Temperature | °C |  |  |  |  |  |  |
| MOTOR |
| 15 | Power | kW |  |  |  |  |  |  |
| 16 | Voltage | V |  |  |  |  |  |  |
| 17 | Current | A |  |  |  |  |  |  |
| 18 | Frequency | Hz |  |  |  |  |  |  |
| 19 | Shaft Speed | rpm |  |  |  |  |  |  |
| 20 | Calculated Efficiency of Pump (Refer to Appendix C) | % |  |  |  |  |  |  |
| BEARING AND WINDING TEMPERATURES (IF AVAILABLE) |
| 21 | Motor NDE | °C |  |  |  |  |  |  |
| 22 | Motor DE | °C |  |  |  |  |  |  |
| 23 | Pump DE | °C |  |  |  |  |  |  |
| 24 | Pump NDE | °C |  |  |  |  |  |  |
| BEARING VIBRATION LEVELS (IF AVAILABLE) |
| 25 | Motor NDE (Vert.) | mm/s RMS |  |  |  |  |  |  |
| 26 | Motor NDE (Horiz.) | mm/s RMS |  |  |  |  |  |  |
| 27 | Motor NDE (Axial) | mm/s RMS |  |  |  |  |  |  |
| 28 | Motor DE (Vert.) | mm/s RMS |  |  |  |  |  |  |
| 29 | Motor DE (Horiz.) | mm/s RMS |  |  |  |  |  |  |
| 30 | Motor DE (Axial) | mm/s RMS |  |  |  |  |  |  |
| 31 | Pump DE (Vert.) | mm/s RMS |  |  |  |  |  |  |
| 32 | Pump DE (Horiz.) | mm/s RMS |  |  |  |  |  |  |
| 33 | Pump DE (Axial) | mm/s RMS |  |  |  |  |  |  |
| 34 | Pump NDE (Vert.) | mm/s RMS |  |  |  |  |  |  |
| 35 | Pump NDE (Horiz.) | mm/s RMS |  |  |  |  |  |  |
| 36 | Pump NDE (Axial) | mm/s RMS |  |  |  |  |  |  |

Notes:

- Manufacturer recommended limits.

- Time 0 = the time of the first set of readings (once the pump is operating at its design duty point).

APPENDIX C – EVALUATION OF TEST VALUES

Flow Rate Q

The measured values from magnetic flowmeter (m3/hour)

Total Head H

pb [Pa] Atmospheric pressure

pd [Pa] Static pressure on discharge side, related to shaft centreline of pump

ps [Pa] Static pressure at suction side, related to shaft centreline of pump

zd, zs [m] Height difference between measurement device and shaft centreline on suction and discharge side

HY [m] Height difference between the reference planes of suction and discharge side (geodetic head)

HV [m] Head losses, the sum of all suction and discharge losses

vs [m/s] Velocity in the suction pipe at the measuring point =  Q/As

vd [m/s] Velocity in the discharge pipe at the measuring point = Q/Ad

ρs [kg/m³] Density of fluid (water) on suction side at Ts and ps taken from VDI Table of Steam Properties

ρd [kg/m³] Density of fluid (water) on discharge side at Td and pd taken from VDI Table of Steam Properties

g [m/s²] Gravitational constant

Pump Efficiency

Q [m³/h] Flow rate

H [m] Total head

ρm [kg/m³] Average density of fluid (water) taken from VDI Table of Steam Properties

g [m/s²] Gravitational constant

Pp [kW] Pump input power