| All ITR documents to be completed & witnessed by competent person/s Compliance to be achieved to contract requirements and all latest versions of applicable standards |
| --- |
| 1. REFERENCE INFORMATION |
| INSPECTION DATA | ASSET DATA |
| PROJECT NAME: | MANUFACTURER: |
| LOCATION: | INSPECTION DATE |
| INSPECTOR NAME: |  |
| PROJECT / CONTRACT NO: | DESIGN CRITERIA: |
| ATTENDEES: |

| 1. REFERENCE INFORMATION |
| --- |
| INSPECTION DATA | ASSET DATA |
| PROJECT NAME: | MANUFACTURER: |
| LOCATION: | MF SERIAL NO: |
| INSPECTION DATE: | WC FLER / TAG NO: |
| INSPECTOR NAME: | TYPE / MODEL NO / SIZE: |
| PROJECT / CONTRACT NO: | DESIGN CRITERIA: |
| ATTENDEES: |

| 2. INSPECTION PREPARATION |
| --- |
|  | OSH compliance requirements. |
|  | Obtain QA / QC documentation (review outstanding items). |
|  | Relevant Water Corporation standards. |
|  | Relevant Australian Standards. |
|  | Supporting contract documentation / approved drawings. |
|  | Provision of required test equipment. |
|  | Provision of required test reports and certificates; i.e. hydrostatic test, material certificates, etc. |

| 3. INSPECTION | YES | NO | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- |
| GENERAL |
| 1 | Locate and verify that name plate/label details match specification and contract requirements |  |  |  | Check: Make/Model/Connection size/Serial number/Duty Flow/Duty Head/Speed/Impeller Diam/Seal model/NPSH3@duty/Duty Power/Year of Manufacture |
| 2 | Casting and machined faces free of sharp edges, burrs and defects? |  |  |  |  |
| 3 | Mating faces match marked and dowelled? |  |  |  |  |
| 4 | Confirm if O&M Manuals have been provided (hardcopy / softcopy) |  |  |  | Hardcopy / softcopy? (please circle) |
| 5 | Shipping stops and temporary bracing removed |  |  |  |  |
| MATERIALS AND ARRANGEMENT |
| 6 | Verify construction materials with material certs, specification and relevant drawings |  |  |  | Check Bowl/Impeller/Shaft/Wear Rings/Shroud |
| 7 | For seawater application ensure all materials of construction are non-corrosive |  |  |  |  |
| 8 | Confirm Major dimensions correct per drawing |  |  |  | Attach a copy of the pump-set drawing to this record sheet highlighting on the drawing which dimensions were checked. |
|  | Suction (Inlet) Nozzles |  |  |  |  |
| 9 | - Flange standard correct? |  |  |  | Flange face: FF / RF |
| 10 | - Diameter correct? |  |  |  | Class: |
| 11 | - Pitch circle diameter correct? |  |  |  | PCD: _____________ mm |
| 12 | - Number and diameter of bolt holes correct? |  |  |  | No.:__________ Dia.:__________ mm |
|  | Discharge (Outlet) Nozzles |  |  |  |  |
| 13 | - Flange standard correct? |  |  |  | Flange face: FF / RF |
| 14 | - Diameter correct? |  |  |  | Class: |
| 15 | - Pitch circle diameter correct? |  |  |  | PCD: _____________ mm |
| 16 | - Number and diameter of bolt holes correct? |  |  |  | No.:__________ Dia.:__________ mm |
|  | Inlet and Outlet Adaptor |  |  |  |  |
| 17 | Confirm adaptor flange detail matches pump suction and discharge nozzles |  |  |  |  |
|  | Stage Casing/Bowl |  |  |  |  |
| 18 | Confirm each stage casing bowl has a integrated diffuser |  |  |  |  |
| 19 | Confirm bowl wear rings are renewable/replaceable |  |  |  |  |
| 20 | Confirm the seals are correct as per drawings and specifications |  |  |  |  |
|  | Impeller and Shaft |  |  |  |  |
| 21 | Ensure number of vanes (if accessible) is correct as per drawing and specifications |  |  |  |  |
| 22 | Ensure vane arrangement is matched to bowl diffuser arrangement |  |  |  |  |
| 23 | Confirm the fastening method of impeller to shaft is correct as per drawing and specifications |  |  |  | Lock nut/Keyed/Locking Collet |
| 24 | Confirm shaft is common through bowl and impeller |  |  |  |  |
|  | Non-return Valve |  |  |  |  |
| 25 | Confirm valve is poppet type and suitable operation in vertical position |  |  |  |  |
| 26 | Confirm valve is installed on pump outlet |  |  |  |  |
| 27 | Confirm valve outlet is internally threaded |  |  |  |  |
|  | Shroud |  |  |  |  |
| 28 | Check cooling shroud is fitted to motor end of the pump via an adaptor fitting and fasteners |  |  |  |  |
|  | Inlet Strainer |  |  |  |  |
| 29 | Confirm inlet strainer is correct as per drawings and specification |  |  |  | Aperture Size……..mm |
|  | Drive Assembly |  |  |  |  |
| 30 | Ensure couplings or splines of shaft to motor is per drawing and specification |  |  |  |  |
| 31 | Confirm motor details are correct as per drawing and specification DS 26 |  |  |  | Check Speed/Power/Poles/Phase/Freq/IP rating |
|  | Appurtenances |  |  |  |  |
| 32 | Ensure any lifting eyes (bowl, motor) suitably rated and fitted? |  |  |  |  |
| 33 | Ensure any auxiliary piping (if applicable) is fitted? |  |  |  |  |
| 34 | Pressure tappings fitted where applicable? |  |  |  |  |
| 35 | Confirm bosses are provided for all tapping points in the pump bowl casing |  |  |  |  |
| 36 | Bearing housing temperature and vibration sensor mounting holes drilled and tapped? |  |  |  |  |

| 4. TEST | PASS | FAIL | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- |
| 1 | Confirm Material certificates are acceptable |  |  |  |  |
| 2 | Confirm Rotating element balance certificate meets required grade |  |  |  |  |
| 3 | Confirm Hydrostatic test certificates are acceptable against contract and specification requirements |  |  |  |  |
| 4 | Confirm Performance test results verify duty guarantees and testing undertaken to relevant AS/ISO standards |  |  |  |  |
| 5 | Confirm Vibration test results meet contract and specification requirements |  |  |  |  |
| 6 | Confirm Noise level test results meet contract and specification requirements |  |  |  |  |

| 5. COATINGS INSPECTION | YES | NO | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- |
| 1 | Verified construction materials with specification and relevant drawings |  |  |  | Substrate material: |
| 2 | Review surface pre-treatment and/or preparation procedure (circle PH: Epoxy Coating on Steel/Cast Iron or state Other) |  |  |  | A1/ OTHER _________________ |
| 3 | Verify coating system and specification ensuring that product is approved for purpose |  |  |  |  |
| 4 | Ensure that surface preparation was acceptable and free from contaminants prior to coating/complies to spec Consider dust and spent abrasive, oil and contamination, flash rusting, slag, porosity, weld spatter, sharp edges, free from laminations, free from burrs etc |  |  |  | Class of surface finish (if known): Profile (if known): Coating application (if known): |
| 5 | Consider if conditions acceptable for testing. Surface temperature should be least 3ºC above dew point and relative humidity less than 85 % before testing |  |  |  | Conditions: |
| 6 | Fully cured coating system should be adherent while in their service condition (Method AS 3894.9) |  |  |  | Failure force (if known): |
| 7 | Assess degree of cure and hardness of coating is acceptable (method AS 3894.4). Allow sufficient drying and curing of the coating prior conducting testing. The length of time shall be obtained from the coating manufacture. |  |  |  | Method used: |
| 8 | Checked that flange faces are clean and are free from any defects resulting from corrosion or any other cause |  |  |  |  |
| 9 | Visually inspect surfaces and ensure is adequately clean and dry prior to testing |  |  |  | Method/chemicals used: |
| 10 | Check internal coating type and verify in accordance with relevant specification (circle D1: Epoxy Coating on Steel/Cast Iron or state, A1: Protective Coating on Steel/Cast Iron or state Other) |  |  |  | A1/D1 / OTHER _____________ |
| 11 | Visually inspect condition of internal coating appearance including uniformity, colour and free from any defect that could impair performance and/or appearance of coating. |  |  |  |  |
| 12 | Check external coating type and verify in accordance with relevant specification (circle PH: Epoxy Coating on Steel/Cast Iron or state, PA: Protective Coating on Steel/Cast Iron or state Other ) |  |  |  | PA / PH / OTHER _____________ |
| 13 | Visually inspect condition of external coating appearance including uniformity, colour and free from any defect that could impair performance and/or appearance of coating. |  |  |  |  |
| 14 | Calibrate thickness tester to standard of uniform and calibrated thickness, covering appropriate range of film thicknesses to be measured |  |  |  | Method/instrument used: |
| 15 | Visually inspect and measure dry film thickness (DFT) in at least 10 locations on coated surfaces. Record values, ensure compliance with spec and record in table below (note that Flange Thickness is not considered acceptable if not within minimum – maximum range) |
| 16 | Ensure coating fully cured prior continuity testing by checking datasheet for required time to full cure or other appropriate test method |  |  |  | Temp/time: Test method: |
| 17 | Calibrate holiday detector (spark tester) electrode with appropriate volt meter which has been laboratory calibrated within the last 2 years to proposed voltage. Record brand and model of spark tester to be used. |  |  |  | Brand/model used: |
| 18 | Carry out spark test on internal coating in accordance to AS 3894.1 Continuity testing of non-conductive coating – High Voltage (brush) method. Specify voltage at which test is carried out. |  |  |  | Test Voltage: V |
| 19 | Carry out spark test on external coating accordance to AS 3894.1 Continuity testing of non-conductive coating – High Voltage (brush) method. Specify voltage at which test is carried out. |  |  |  | Test Voltage: V |
| 20 | Asset passes continuity testing with zero defects (including pinholes, holidays, cracks and other discontinuities) detected in finished coating for immersed/buried conditions and/or subsequent repairs have been carried out before being placed in service. |  |  |  |  |

| Coating Thickness: | Internal (micrometers): | External (micrometers): | Flange (micrometers ): | Complies with Spec? |
| --- | --- | --- | --- | --- |
| Specified min |  |  |  | N/A |
| Specified max |  |  |  | N/A |
| Measured 1 |  |  |  |  |
| Measured 2 |  |  |  |  |
| Measured 3 |  |  |  |  |
| Measured 4 |  |  |  |  |
| Measured 5 |  |  |  |  |
| Measured 6 |  |  |  |  |
| Measured 7 |  |  |  |  |
| Measured 8 |  |  |  |  |
| Measured 9 |  |  |  |  |
| Measured 10 |  |  |  |  |
| Average |  |  |  |  |
| Note any comment or variation to test procedure that will assist in interpretation of results: |

Refer to AS/NZS 1627 series for Metal Finishing – Preparation and Pre-treatment of Surfaces

2 Refer to AS 3894.7 for practical procedure for Determination of Surface Temperature of metal surfaced (pre-coating)

3 Refer to AS 3894.3 methods for Determination of Dry Film Thickness

4 Method AS 3894.3 refers Determination of Dry Film Thickness

| 6. REMARKS / REMEDIAL / FOLLOW UP ACTIONS | ACTION BY | TARGET DATE | STATUS |
| --- | --- | --- | --- |

| 7. SIGNOFFS |
| --- |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |

# POST TRANSPORTATION INSPECTION

- Inspection to be completed at point of delivery

- If a supply verification was not completed at the manufacturer, both supply verification and post transportation inspection should be completed at point of delivery.

| 8. POST TRANSPORTATION REMARKS / REMEDIAL / FOLLOW UP ACTIONS | ACTION BY | TARGET DATE |
| --- | --- | --- |

| 9. SIGNOFFS |
| --- |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |

# Footnotes

Refer to AS 1627 series for Metal Finishing – Preparation and Pre-treatment of Surfaces

Refer to AS 3894.7 for practical procedure for Determination of Surface Temperature of metal surfaced (pre-coating)

Refer to AS 3894.3 methods for Determination of Dry Film Thickness

Method AS 3894.3 refers Determination of Dry Film Thickness