| All ITR documents to be completed & witnessed by competent person/s Compliance to be achieved to contract requirements and all latest versions of applicable standards |
| --- |
| 1. REFERENCE INFORMATION |
| INSPECTION DATA | ASSET DATA |
| PROJECT NAME: | MANUFACTURER: |
| LOCATION: | INSPECTION DATE |
| INSPECTOR NAME: |  |
| PROJECT / CONTRACT NO: | DESIGN CRITERIA: |
| ATTENDEES: |

| 2. INSPECTION PREPARATION |
| --- |
|  | OSH compliance requirements. |
|  | Obtain QA / QC documentation (review outstanding items). |
|  | Relevant Water Corporation standards i.e. DS 31-01 |
|  | Relevant Australian Standards. |
|  | Supporting contract documentation / approved drawings. |
|  | Provision of required test equipment. |
|  | Provision of required test reports and certificates |

| 3. INSPECTION | YES | NO | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- |
| GENERAL AND PRE-INSTALLATION |
| 1 | Confirm that the dismantling joint location is correct as per drawings |  |  |  |  |
| 2 | Confirm supply verification complete |  |  |  |  |
| 3 | Mating pipe pressure class as per specification? |  |  |  | Class: |
| 4 | Mating pipe diameter as per specification? |  |  |  | Diameter: _____________mm |
| 5 | Confirm pipe adequately supported |  |  |  |  |
| 6 | Pipe material as per specification? |  |  |  | Material: |
| 7 | Mating pipes clean and deburred? |  |  |  |  |
| 8 | Mating pipes aligned to within dismantling joint manufacturer’s recommendations? |  |  |  | Manufacturers max misalignment: _____________mm Measured misalignment: _____________mm Manufacturers max angular deflection: __________deg Measured angular deflection: __________deg |
| 9 | Mating pipes differential O.D. within joint manufactures tolerances (including pipe ovality)? |  |  |  | Manufacturers max differential OD: _____________mm Measured differential OD: _____________mm |
| 10 | Confirm distance between pipes to be joined is within dismantling joint manufacturer’s recommendations |  |  |  | Distance: _____________mm |
| INSTALLATION |
| 11 | Verify that all bolts have been torqued to dismantling joint manufacturer’s recommendations |  |  |  | Final bolt torques: _____________Nm |
| 12 | Conductivity clips installed correctly? |  |  |  |  |
| 13 | Assembled diameter of dismantling joint as per joint manufacturer’s recommendations? |  |  |  | Diameter: _____________mm |
| 14 | Confirm dismantling joint is centred over mating pipes |  |  |  |  |
| RESTRAINING JOINT (IF APPLICABLE) |
| 15 | Check that correct isolating bolt sleeves and washers have been installed according to bolt size |  |  |  |  |
| 16 | Confirm all bolts sizes, material and grade are correct |  |  |  | Size: ________ Material: __________ Grade: 4.6 8.8 Other: _______ |
| 17 | Confirm that associated nut grade is correct |  |  |  | Grade: 5 8 Other __________ |
| 18 | Confirm correct protrusion of bolt threads past nut |  |  |  | Protrusion: _____________________ |
| 19 | Confirm correct bolt tightening sequence has been followed |  |  |  |  |
| 20 | Verify that all bolts have been torqued correctly |  |  |  | Final bolt torques: _____________Nm |
| 21 | Verify that torque wrench / machine used is calibrated |  |  |  | Calibration certificate date: _________ |
| 22 | For buried pipe joints ensure stripping of HDPE pipe coating and wrapping of joint meets design standards |  |  |  |  |

| 4. TESTING (IF APPLICABLE) | YES | NO | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- |
| 1 | Mating pipe axial movement within manufacturers tolerances after testing |  |  |  | Manufacturers max allowed movement: _____________mm Measured movement: _____________mm Test pressure: _____________mAHD |

| 5. REMARKS / REMEDIAL / FOLLOW UP ACTIONS | ACTION BY | TARGET DATE | STATUS |
| --- | --- | --- | --- |

| 6. SIGNOFFS |
| --- |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |