- All ITR documents to be completed & witnessed by competent person/s

- Compliance to be achieved to contract requirements and all latest versions of applicable standards

| 1. REFERENCE INFORMATION |
| --- |
| INSPECTION DATA | ASSET DATA |
| PROJECT NAME: | MANUFACTURER: |
| LOCATION: | MF SERIAL NO: |
| INSPECTION DATE: | WC FLER / TAG NO: |
| INSPECTOR NAME: | TYPE / MODEL NO / SIZE: |
| PROJECT / CONTRACT NO: | DESIGN CRITERIA: |
| ATTENDEES: |

| 2. INSPECTION PREPARATION |
| --- |
|  | OSH compliance requirements. |
|  | Obtain QA / QC documentation (review outstanding items). |
|  | Relevant Water Corporation standards. |
|  | Relevant Australian Standards. |
|  | Supporting contract documentation / approved drawings. |
|  | Provision of required test equipment (portable vibration monitor and temperature sensor). |
|  | Provision of required test reports and certificates |
|  | Provision of completed construction verification |

| 3. INSPECTION PRELIMINARIES | YES | NO | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- |
| 1 | “Punchlist” reviewed and free of significant defects preventing asset pre-commissioning? |  |  |  |  |
| 2 | Hazard identification and risk assessment for asset pre-commissioning complete? |  |  |  |  |
| 3 | Electrical construction and pre-commissioning ITPs complete? |  |  |  |  |
| 4 | Mechanical and electrical site specific pre-requisite ITPs complete? |  |  |  |  |

*Contents of Section 4 (Inspection) and Section 5 (Test) are Asset Specific and shall reflect relevant SPS / Australian Standard(s) where practicable. Entries shall also be worded to reflect the procedures involved in a step-by-step manner; i.e. “Conduct visual inspection and ensure pre-start photographs are taken”, “Extract bearing housing covers to expose bearings and full shaft length”.

| 4. INSPECTION | YES | NO | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- |
| GENERAL |
| 1 | Injection point higher than solution supply tank to prohibit gravity feeding unless suitable back pressure is present at injection point? |  |  |  |  |
| ANCILLARY AND TEMPORARY EQUIPMENT |
| 2 | Foot valve and strainer installed in solution supply tank? |  |  |  |  |
| 3 | Foot valve and strainer installed at least (2-5cm) above bottom of solution supply tank |  |  |  |  |
| 4 | Back pressure valve installed of correct pressure rating to match pump back pressure? |  |  |  |  |
| 5 | Is an Anti-Siphon valve installed in the discharge line (when pressure in discharge line is below atmospheric) |  |  |  |  |
| 6 | Is a back pressure/injection valve installed to maintain metering performance? |  |  |  |  |
| 7 | Is back pressure/injection valve of correct pressure rating? |  |  |  |  |
| 8 | Flushing device installed of correct pressure rating to match pump back pressure? |  |  |  |  |
| 9 | For chemicals prone to formation of precipitation is a mixer installed in tank? |  |  |  |  |
| 10 | To ensure rapid dilution at injection point, is an injection fitting installed central to flow stream of line being treated ? |  |  |  |  |
| 11 | Is suction pulsation dampener installed to manufacturer’s recommendations and of correct pressure rating? |  |  |  |  |
| 12 | Is discharge pulsation dampener installed to manufacturer’s recommendations and of correct pressure rating? |  |  |  |  |
| 13 | Is a pressure relief valve installed to manufacturer’s recommendations and of correct pressure rating? |  |  |  |  |
| 14 | Is a flow measuring glass/rotameter installed to manufacturer’s recommendations and of correct pressure rating? |  |  |  |  |
| 15 | Temporary instruments (if required) installed? (eg. vibration transducers, flow meters, pressure gauges) |  |  |  |  |
| HYDRAULICS |
| 16 | Is a flooded suction available to pump? (Recommended for chemicals prone to production of air bubbles ie. sodium hypochlorite ) |  |  |  |  |
| 17 | Is solution tank adequately filled for period of operation? |  |  |  |  |
| 18 | All pump suction valves open? |  |  |  |  |
| 19 | Open flow path available for pumped liquid once the discharge valve is opened? |  |  |  |  |
| 20 | Instrument impulse lines primed and vented? |  |  |  |  |
| 21 | All connections along flow path hydraulically tight (no leaks)? |  |  |  |  |
| 22 | System static head conditions suitable for pump operation? |  |  |  |  |
| ACCESS |
| 23 | Area around pumpset clean, free of debris and barricaded off from other works (if required)? |  |  |  |  |
| 24 | Emergency stop pushbutton accessible? |  |  |  |  |

| 5. TEST | YES | NO | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- |
| PRESSURE TEST |
| 1 | With the isolation suction and discharge valves closed pressure test to the maximum line pressure. Check for leaks |  |  |  |  |
| PERFORMANCE ASSESSMENT |
| 2 | “Bump” start the pump motor to ensure direction of rotation of motor is correct |  |  |  |  |
| 3 | Does pump performance meet its specification in terms of dosing rate? |  |  |  |  |
| 4 | Pitch and level of noise emanating from pump, motor and bearings acceptable? |  |  |  |  |
| 5 | Pump and pipework connections hydraulically tight (no leaks)? |  |  |  |  |
| 6 | Are there any signs of cavitation? |  |  |  |  |

Sections 6 & 7 to be retained in all ITPs.

| 6. REMARKS / REMEDIAL / FOLLOW UP ACTIONS | ACTION BY | TARGET DATE | STATUS |
| --- | --- | --- | --- |

| 7. SIGNOFFS |
| --- |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |

APPENDIX A – SITE SPECIFIC PRE-REQUISITES

| A1. MECHANICAL PRE-REQUISITES | DONE | NO | ITR / DOCUMENT REF. |
| --- | --- | --- | --- |
|  |  |  |  | ITP-SV-M-PUMP |
|  |  |  |  | ITP-CV-M-PUMP |

APPENDIX A – SITE SPECIFIC PRE-REQUISITES (cont’d)

| A2. ELECTRICAL PRE-REQUISITES | DONE | NO | ITR / DOCUMENT REF. |
| --- | --- | --- | --- |

APPENDIX B – PUMP PERFORMANCE RECORD SHEET

| # | PARAMETER | UNITS | MAX. LIMIT (Note 1) | PRE START-UP | T0 (Note 2) | T1 | T2 | T3 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| GENERAL |
| 1 | Time | Hrs:Min |  |  |  | +5 min | +10 min | +15 min |
| 2 | Ambient Temperature | °C |  |  |  |  |  |  |
| 3 | Atmospheric Pressure | Pa |  |  |  |  |  |  |
| 4 | Pipe Inside Diameters | mm |  |  |  |  |  |  |
| 5 | Electrical String Efficency (TX,VSD,motor) | % |  |  |  |  |  |  |
| PUMP |
| 5 | Suction Pressure | Pa |  |  |  |  |  |  |
| 6 | Suction Head | m |  |  |  |  |  |  |
| 7 | Discharge Pressure | Pa |  |  |  |  |  |  |
| 4 | Discharge Head | m |  |  |  |  |  |  |
| 5 | Calculated Pump Head (Refer to Appendix C) | m |  |  |  |  |  |  |
| 6 | Flowrate | m3/hr |  |  |  |  |  |  |
| 7 | Suction Temperature | °C |  |  |  |  |  |  |
| 8 | Discharge Temperature | °C |  |  |  |  |  |  |
| MOTOR |
| 7 | Power | kW |  |  |  |  |  |  |
| 8 | Voltage | V |  |  |  |  |  |  |
| 9 | Current | A |  |  |  |  |  |  |
| 10 | Frequency | Hz |  |  |  |  |  |  |
| 11 | Shaft Speed | rpm |  |  |  |  |  |  |
| 12 | Calculated Efficiency of Pump (Refer to Appendix C) | % |  |  |  |  |  |  |
| BEARING TEMPERATURES |
| 12 | Motor NDE | °C |  |  |  |  |  |  |
| 13 | Motor DE | °C |  |  |  |  |  |  |
| 14 | Pump DE | °C |  |  |  |  |  |  |
| 15 | Pump NDE | °C |  |  |  |  |  |  |
| BEARING VIBRATION LEVELS |
| 16 | Motor NDE (Vert.) | mm/s RMS |  |  |  |  |  |  |
| 17 | Motor NDE (Horiz.) | mm/s RMS |  |  |  |  |  |  |
| 18 | Motor NDE (Axial) | mm/s RMS |  |  |  |  |  |  |
| 19 | Motor DE (Vert.) | mm/s RMS |  |  |  |  |  |  |
| 20 | Motor DE (Horiz.) | mm/s RMS |  |  |  |  |  |  |
| 21 | Motor DE (Axial) | mm/s RMS |  |  |  |  |  |  |
| 22 | Pump DE (Vert.) | mm/s RMS |  |  |  |  |  |  |
| 23 | Pump DE (Horiz.) | mm/s RMS |  |  |  |  |  |  |
| 24 | Pump DE (Axial) | mm/s RMS |  |  |  |  |  |  |
| 25 | Pump NDE (Vert.) | mm/s RMS |  |  |  |  |  |  |
| 26 | Pump NDE (Horiz.) | mm/s RMS |  |  |  |  |  |  |
| 27 | Pump NDE (Axial) | mm/s RMS |  |  |  |  |  |  |

Notes:

- Manufacturer recommended limits.

- Time 0 = the time of the first set of readings (once the pump is operating at its design duty point).

APPENDIX C – EVALUATION OF TEST VALUES

Flow Rate Q

The measured values from magnetic flowmeter (m3/hour)

Total Head H

pb [Pa] Atmospheric pressure

pd [Pa] Static pressure on discharge side, related to shaft centreline of pump

ps [Pa] Static pressure at suction side, related to shaft centreline of pump

zd, zs [m] Height difference between measurement device and shaft centreline on suction and discharge side

HY [m] Height difference between the reference planes of suction and discharge side (geodetic head)

HV [m] Head losses, the sum of all suction and discharge losses

vs [m/s] Velocity in the suction pipe at the measuring point =  Q/As

vd [m/s] Velocity in the discharge pipe at the measuring point = Q/Ad

ρs [kg/m³] Density of fluid (water) on suction side at Ts and ps taken from VDI Table of Steam Properties

ρd [kg/m³] Density of fluid (water) on discharge side at Td and pd taken from VDI Table of Steam Properties

g [m/s²] Gravitational constant

Pump Efficiency

Q [m³/h] Flow rate

H [m] Total head

ρm [kg/m³] Average density of fluid (water) taken from VDI Table of Steam Properties

g [m/s²] Gravitational constant

Pp [kW] Pump input power