| All ITR documents to be completed & witnessed by competent person/s Compliance to be achieved to contract requirements and all latest versions of applicable standards |
| --- |
| 1. REFERENCE INFORMATION |
| INSPECTION DATA | ASSET DATA |
| PROJECT NAME: | MANUFACTURER: |
| LOCATION: | INSPECTION DATE |
| INSPECTOR NAME: |  |
| PROJECT / CONTRACT NO: | DESIGN CRITERIA: |
| ATTENDEES: |

| 1. REFERENCE INFORMATION |
| --- |
| INSPECTION DATA | ASSET DATA |
| PROJECT NAME: | MANUFACTURER: |
| LOCATION: | MF SERIAL NO: |
| INSPECTION DATE: | WC FLER / TAG NO: |
| INSPECTOR NAME: | TYPE / MODEL NO / SIZE: |
| PROJECT / CONTRACT NO: | DESIGN CRITERIA: |
| ATTENDEES: |

| 2. INSPECTION PREPARATION |
| --- |
|  | OSH compliance requirements. |
|  | Obtain QA / QC documentation (review outstanding items). |
|  | Relevant Water Corporation standards. |
|  | Relevant Australian Standards. |
|  | Supporting contract documentation / approved drawings. |
|  | Provision of required test equipment. |
|  | Provision of required test reports and certificates; i.e. hydrostatic test, material certificates, etc. |

| 3. INSPECTION | YES | NO | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- |
| GENERAL |
| 1 | Visually inspect flowmeter installation and verify correct installation as per manufacturer’s recommendations and Water Corp standard drawing EG-20-4-2 |  |  |  |  |
| 2 | Confirm that flowmeter location is correct as per drawings |  |  |  |  |
| 3 | Verify correct orientation / direction of flow for installed valve |  |  |  |  |
| 4 | Number of straight pipe diameters provided upstream and downstream of valve correct? |  |  |  |  |
| 5 | Flowmeter support adequate? |  |  |  |  |
| 6 | Adjacent pipework supported independently of flowmeter? |  |  |  |  |
| 7 | Local upstream and downstream isolation available for flowmeter? |  |  |  |  |
| BOLT-UP & BONDING CABLING |
| 8 | Check that mating flanges are flat, clean and free of irregularities |  |  |  |  |
| 9 | Verify gasket material and thickness on each side of the two off potential equalisation rings is as per drawings and manufacturer recommendations |  |  |  | Material: CMF EPDM Other _____________________ Thickness: _________________mm Note the gasket between ring and pipework flange is an insulating gasket while the gasket between ring and flowmeter maybe an elastomeric gasket depending on manufacturers requirements |
| 10 | Confirm all bolts installed on the flowmeter and that bolt sizes, material and grade are correct |  |  |  | Size: ________ Material: __________ Grade: 4.6 8.8 Other: _______ |
| 11 | Confirm that associated nut grade is correct |  |  |  | Grade: 5 8 Other __________ |
| 12 | Confirm correct protrusion of bolt threads past nut |  |  |  | Protrusion: _____________________ |
| 13 | Confirm correct bolt tightening sequence has been followed |  |  |  |  |
| 14 | Verify bolt torque complies with flowmeter manufacturer’s recommendation. Also verify actual bolt torque applied to each bolt is correct. |  |  |  | Note DS38 bolt torque requirement do not apply for elastomeric lined magnetic flowmeters. Actual bolt torque: _____________Nm |
| 15 | Verify that torque wrench / machine used is calibrated |  |  |  | Calibration certificate date: _________ |
| 16 | Confirm bonding cable is connected between potential equalisation rings and flowmeter flanges both upstream and downstream |  |  |  | Ensure the connection tabs on the potential equalisation ring align with flowmeter studs. |
| 17 | Verify that bonding cable across the flowmeter has been installed between studs located on upstream and downstream adjoining pipework |  |  |  |  |
| ISOLATING JOINTS (*MANDATORY REQUIREMENT ON UPSTREAM AND DOWNSTREAM FLANGE CONNECTIONS) |
| 18 | Check that correct isolating bolt sleeves and washers have been installed and free of cracks |  |  |  |  |
| 19 | Verify that flange to flange electrical isolation is acceptable using according to referenced ITPs |  |  |  | Refer to the following #6467071-v1-CP-MESB-ITP-002 INS JOINTS CE-IT.DOC #6467062-v1-CP-MESB-ITP-001 INS JOINTS RF-IT.DOC #3530465-v1-ITP-CV-M-ISOLATION JOINT.DOC |
| BURIED APPLICATIONS |
| 20 | Verify that a test post has been installed |  |  |  |  |
| 21 | Confirm if a surge diverter has been installed |  |  |  |  |
| 22 | Ensure the flowmeter is waterproofed before backfilling. Until waterproofing is complete avoid any possible immersion of the junction box in water as permanent damage could occur. |  |  |  | Water proofing means: Cables installed Junction box is potted Flange connections wrapped |

| 4. TEST | YES | NO | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- |
| 1 |  |  |  |  | Not applicable mechanically |
| 2 |  |  |  |  |  |
| 3 |  |  |  |  |  |

| 5. COATINGS INSPECTION | YES | NO | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- |
| 1 | Check that valve internal coating is free of damage |  |  |  | Not applicable for elastomeric lined flowmeters |
| 2 | Check that valve external coating is free of damage |  |  |  |  |
| 3 | Confirm that flowmeter flange connection wrapping is satisfactory (buried service only) |  |  |  |  |

| 6. REMARKS / REMEDIAL / FOLLOW UP ACTIONS | ACTION BY | TARGET DATE | STATUS |
| --- | --- | --- | --- |

| 7. SIGNOFFS |
| --- |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |