- All ITR documents to be completed & witnessed by competent person/s

- Compliance to be achieved to contract requirements and all latest versions of applicable standards

| 1. REFERENCE INFORMATION |
| --- |
| INSPECTION DATA | ASSET DATA |
| PROJECT NAME: | MANUFACTURER: |
| LOCATION: | MF SERIAL NO: |
| INSPECTION DATE: | WC FLER / TAG NO: |
| INSPECTOR NAME: | TYPE / MODEL NO / SIZE: |
| PROJECT / CONTRACT NO: | DESIGN CRITERIA: |
| ATTENDEES: |

| 2. INSPECTION PREPARATION |
| --- |
|  | OSH compliance requirements. |
|  | Obtain QA / QC documentation (review outstanding items). |
|  | Relevant Water Corporation standards. |
|  | Relevant Australian Standards. |
|  | Supporting contract documentation / approved drawings. |
|  | Provision of required test equipment. |
|  | Provision of required test reports and certificates; i.e. hydrostatic test, material certificates, etc. |
|  | Provision of completed construction verification |

| 3. INSPECTION PRELIMINARIES | YES | NO | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- |
| 1 | “Punchlist” reviewed and free of significant defects preventing asset pre-commissioning |  |  |  |  |
| 2 | Supply and Construction Verification ITRs complete |  |  |  |  |
| 3 | Hazard identification and risk assessment for asset pre-commissioning complete |  |  |  |  |
| 4 | Mechanical and electrical site-specific pre-requisite ITRs complete |  |  |  |  |

| 4. INSPECTION & TESTING | YES | NO | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- |
| GENERAL |
| 1 | Confirm pressure test has been completed and pipework is free of leaks |  |  |  |  |
| 2 | Ensure power is available for all pumps, instruments, and other equipment |  |  |  |  |
| 3 | Check that the clarifier mechanisms function smoothly. Check central shaft rotation in mitigating potential for fatigue loading of structure / bolts |  |  |  |  |
| 4 | Cross check speed of rake(s) with supplier recommendations |  |  |  |  |
| 5 | Check that the upper rake arm/scraper pushes water into the trough. (Contacts the beach) |  |  |  |  |
| 6 | Check that the torque limits on the gearbox/drive motor of rake arms are correct and function (verify via electrical O/Load cross check) |  |  |  |  |

| 5. REMARKS / REMEDIAL / FOLLOW UP ACTIONS | ACTION BY | TARGET DATE | STATUS |
| --- | --- | --- | --- |

| 6. SIGNOFFS |
| --- |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |