- All ITR documents to be completed & witnessed by competent person/s

- Compliance to be achieved to contract requirements and all latest versions of applicable standards

| 1. REFERENCE INFORMATION |
| --- |
| INSPECTION DATA | ASSET DATA |
| PROJECT NAME: | MANUFACTURER: |
| LOCATION: | MF SERIAL NO: |
| INSPECTION DATE: | WC FLER / TAG NO: |
| INSPECTOR NAME: | TYPE / MODEL NO / SIZE: |
| PROJECT / CONTRACT NO: | DESIGN CRITERIA: |
| ATTENDEES: |

| 2. INSPECTION PREPARATION |
| --- |
|  | OSH compliance requirements. |
|  | Obtain QA / QC documentation (review outstanding items). |
|  | Relevant Water Corporation standards. |
|  | Relevant Australian Standards. |
|  | Supporting contract documentation / approved drawings. |
|  | Provision of required test equipment. |
|  | Provision of required test reports and certificates; i.e. hydrostatic test, material certificates, etc. |

| 3. INSPECTION PRELIMINARIES | YES | NO | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- |
| 1 | “Punchlist” reviewed and free of significant defects preventing asset pre-commissioning |  |  |  |  |
| 2 | Supply Verification ITR complete |  |  |  |  |
| 3 | Hazard identification and risk assessment for asset pre-commissioning complete |  |  |  |  |
| 4 | Mechanical and electrical site-specific pre-requisite ITRs complete |  |  |  |  |

| 4. INSPECTION | YES | NO | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- |
| GENERAL |
| 1 | Conduct visual inspection, and ensure photographs are taken |  |  |  |  |
| 2 | Confirm that the Grit Trap Agitator is installed as per drawings, and is horizontally level |  |  |  |  |
| 3 | Identification plate, and installed unit matches plate |  |  |  |  |
| 4 | Verify that torque wrench / machine used is calibrated |  |  |  | Calibration certificate date: _________ |
| CHAMBER & BAFFLES |
| 5 | Check Chamber & Baffles are to drawings |  |  |  |  |
| 6 | Check inlet ramp geometry and that the inlet baffles and spoiler are fitted correctly |  |  |  | PISTA – M12 & Torque: 35 Nm |
| 7 | Check fitting of outlet baffles/orifice and braces correct |  |  |  | PISTA – M16 & Torque: 95 Nm |
| 8 | Check grouting of grit hopper |  |  |  |  |
| 9 | Check grit fluidiser vane clearance with bottom of grit chamber and grout |  |  |  | Clearance: _________________mm PISTA – (100 – 500 mm) |
| 10 | Check grit hopper floor plate is recessed correctly |  |  |  |  |
| AGITATOR DRIVE UNIT |
| 11 | Check drive unit size is correct |  |  |  |  |
| 12 | Check drive unit is level |  |  |  |  |
| 13 | Check all anchor bolts and grouting is complete |  |  |  | PISTA – M12 & Torque: 35 Nm |
| 14 | Check all central drive tube bolts are torqued up and seal is in place |  |  |  | PISTA – ½” & Torque: 95 Nm |
| 15 | Check central drive tube alignment with bottom of grit chamber and top chamber floor plates |  |  |  | PISTA – M16 & Torque: 95 Nm |
| 16 | If no pump is fitted to the drive tube, verify that a blanking flange seals the drive tube. Otherwise ensure there is a sealing plate for the pump suction piping bolted to the top of the drive tube |  |  |  |  |
| 17 | Check upper steel floor plates are fitting into floor correctly |  |  |  | PISTA – M12 & Torque: 35 Nm |
| 18 | Propellers set at correct angle for direction of rotation and correct height |  |  |  | PISTA – Positioned less than 200mm above the floor to their centre line (80 – 100mm) to the bottom of the blades |
| 19 | Verify Grit Fluidiser Helix’s are in correct orientation |  |  |  |  |
| 5. COATINGS INSPECTION | YES | NO | N/A | COMMENTS/DETAILS |
| 1 | Not applicable |  |  |  |  |

| 6. REMARKS / REMEDIAL / FOLLOW UP ACTIONS | ACTION BY | TARGET DATE | STATUS |
| --- | --- | --- | --- |

| 7. SIGNOFFS |
| --- |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |

POST TRANSPORTATION INSPECTION

- Inspection to be completed at point of delivery

- If a supply verification was not completed at the manufacturer, both supply verification and post transportation inspection should be completed at point of delivery.

| 8. POST TRANSPORTATION REMARKS / REMEDIAL / FOLLOW UP ACTIONS | ACTION BY | TARGET DATE |
| --- | --- | --- |

| 9. SIGNOFFS |
| --- |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |