- All ITR documents to be completed & witnessed by competent person/s

- Compliance to be achieved to contract requirements and all latest versions of applicable standards

| 1. REFERENCE INFORMATION |
| --- |
| INSPECTION DATA | ASSET DATA |
| PROJECT NAME: | MANUFACTURER: |
| LOCATION: | MF SERIAL NO: |
| INSPECTION DATE: | WC FLER / TAG NO: |
| INSPECTOR NAME: | TYPE / MODEL NO / SIZE: |
| PROJECT / CONTRACT NO: | DESIGN CRITERIA: |
| ATTENDEES: |

| 2. INSPECTION PREPARATION |
| --- |
|  | OSH compliance requirements. |
|  | Obtain QA / QC documentation (review outstanding items). |
|  | Relevant Water Corporation standards. |
|  | Relevant Australian Standards. |
|  | Supporting contract documentation / approved drawings. |
|  | Provision of required test equipment. |
|  | Provision of required test reports and certificates, i.e. hydrostatic test, material certificates, etc. |

| 3. INSPECTION PRELIMINARIES | YES | NO | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- |
| 1 | “Punchlist” reviewed and free of significant defects preventing asset pre-commissioning |  |  |  |  |
| 2 | Supply Verification ITR complete |  |  |  |  |
| 3 | Hazard identification and risk assessment for asset pre-commissioning complete |  |  |  |  |
| 4 | Mechanical and electrical site-specific pre-requisite ITRs complete |  |  |  |  |

| 4. INSPECTION | YES | NO | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- |
| GENERAL |
| 1 | Conduct visual inspection, and ensure photographs are taken |  |  |  |  |
| 2 | Identification plate details and installed unit match plate |  |  |  |  |
| 3 | Verify that torque equipment is suitably calibrated |  |  |  | Calibration certificate I.D. & Date: ___________________ |
| 4 | Verify machine foundations are level |  |  |  |  |
| 5 | Check all anchor fixings sizes, centres and grouting details are correct |  |  |  |  |
| 6 | Confirm that the Screw Press installation is as per drawings, and its legs are horizontally level |  |  |  |  |
| 7 | Verify space requirements around asset is met |  |  |  |  |
| BOLT-UP |
| PIPE & MOTOR CONNECTIONS |
| 8 | Check that mating flanges are flat, clean, and free of irregularities |  |  |  |  |
| 9 | Verify gasket material and thickness |  |  |  | Material: CMF EPDM Other _____________________ Thickness: _________________mm |
| 10 | Confirm all bolts, bolt sizes, material, and grade are correct |  |  |  | Size: ________ Material: __________ Class: 4.6 8.8 Other: ______ |
| 11 | Confirm that associated nut grade is correct |  |  |  | Grade: 5 8 Other ________ |
| 12 | Confirm correct protrusion of bolt threads past nut |  |  |  | Protrusion (mm): _____________________ |
| 13 | Confirm correct bolt tightening sequence has been followed |  |  |  |  |
| 14 | Verify bolt torque requirements comply with Vendor recommendations. Verify actual bolt torque applied to each bolt is correct |  |  |  | Recommended bolt torque: _____________Nm Actual bolt torque: _____________Nm |
| 15 | If required by design, verify that flange isolation materials have been installed correctly (as applicable) |  |  |  |  |
| 16 | Verify that bonding link(s) have been installed correctly (as applicable) |  |  |  |  |
| AUGER |
| 17 | Check all central drive tube bolts are torqued up and seal is in place |  |  |  |  |
| COMPRESSED AIR AND WATER |
| 18 | Check correct air pressure is supplied as per manufacturer’s requirement |  |  |  | Pressure: __________ bar |
| 19 | Check correct water pressure is supplied as per manufacturer’s requirement |  |  |  | Pressure: __________ bar |
| POLYMER INJECTION, FILTRATE, AND WASH LINES |
| 20 | Polymer line is connected as per drawings |  |  |  |  |
| 21 | Filtrate line is connected as per drawings |  |  |  |  |
| 22 | Drain line is connected as per drawings |  |  |  |  |
| 23 | Wash line is connected as per drawings |  |  |  |  |
| MOTOR AND ELECTRICS |
| 24 | Verify motor coupling is aligned |  |  |  |  |
| 25 | Verify solenoid valve on wash water line is present |  |  |  |  |
| ISOLATING JOINTS (IF REQUIRED FOR DISSIMILAR METALS OR CATHODIC PROTECTION ISOLATION) |
| 26 | Cathodic protection installed (as applicable) |  |  |  |  |
| 27 | Check that correct isolating bolt sleeves and washers have been installed |  |  |  |  |
| 28 | Verify that flange to flange isolation is acceptable |  |  |  |  |
| 29 | Verify that a test post has been installed |  |  |  |  |
| 30 | Confirm if a surge diverter has been installed |  |  |  |  |

| 5. COATINGS INSPECTION | YES | NO | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- |
| 1 | Not applicable |  |  |  |  |

| 6. REMARKS / REMEDIAL / FOLLOW UP ACTIONS | ACTION BY | TARGET DATE | STATUS |
| --- | --- | --- | --- |

| 7. SIGNOFFS |
| --- |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |

POST TRANSPORTATION INSPECTION

- Inspection to be completed at point of delivery

- If a supply verification was not completed at the manufacturer, both supply verification and post transportation inspection should be completed at point of delivery.

| 8. POST TRANSPORTATION REMARKS / REMEDIAL / FOLLOW UP ACTIONS | ACTION BY | TARGET DATE |
| --- | --- | --- |

| 9. SIGNOFFS |
| --- |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |