| All ITR documents to be completed & witnessed by competent person/s Compliance to be achieved to contract requirements and all latest versions of applicable standards |
| --- |
| 1. REFERENCE INFORMATION |
| INSPECTION DATA | ASSET DATA |
| PROJECT NAME: | MANUFACTURER: |
| LOCATION: | INSPECTION DATE |
| INSPECTOR NAME: |  |
| PROJECT / CONTRACT NO: | DESIGN CRITERIA: |
| ATTENDEES: |

* All Pre-Commissioning documents shall contain the following sections (1 – 2) which capture generic asset information

| 2. INSPECTION PREPARATION |
| --- |
|  | OSH compliance requirements. |
|  | Obtain QA / QC documentation (review outstanding items). |
|  | Relevant Water Corporation standards. |
|  | Relevant Australian Standards. |
|  | Supporting contract documentation / approved drawings. |
|  | Provision of required test equipment (portable vibration monitor and temperature sensor). |
|  | Provision of required test reports and certificates |
|  | Provision of completed construction verification |

| 3. INSPECTION PRELIMINARIES | YES | NO | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- |
| 1 | “Punchlist” reviewed and free of significant defects preventing asset pre-commissioning? |  |  |  |  |
| 2 | Hazard identification and risk assessment for asset pre-commissioning complete? |  |  |  |  |
| 3 | Electrical construction and pre-commissioning ITRs complete? |  |  |  |  |
| 4 | Mechanical and electrical site specific pre-requisite ITRs complete? |  |  |  |  |

*Contents of Section 4 (Inspection) and Section 5 (Test) are Asset Specific and shall reflect relevant SPS / Australian Standard(s) where practicable. Entries shall also be worded to reflect the procedures involved in a step-by-step manner; i.e. “Conduct visual inspection and ensure pre-start photographs are taken”, “Extract bearing housing covers to expose bearings and full shaft length”.

| 4& 5. INSPECTION & TESTING | YES | NO | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- |
| GENERAL |
| 1 | Confirm hydro test has been completed and pipework, header and nozzles are free of leaks |  |  |  |  |
| 2 | Confirm availability of sufficient pressure to achieve required spray nozzle pattern and flow rate |  |  |  | Pressure: …..kPa |
| 3 | Confirm bypass line is available if required |  |  |  |  |
| MANUAL OPERATION - APPLIES TO MANUAL CONTROL VALVES AND MANUAL OVERIDE OF ELECTRICALLY ACTUATED CONTROL VALVES (Complete this section if a separate valve PC is not being completed) |
| 4 | Confirm that the valve starting position is closed. Close the valve if not already so |  |  |  |  |
| 5 | Slowly open the valve to fully open and confirm smooth valve operation during opening and that the required force to open the valve is not excessive |  |  |  |  |
| 6 | Confirm that the valve open position indication is correct when in the fully open position |  |  |  | Note gearbox end-stops may need adjustment if the valve does not fully open. |
| 7 | Slowly close the valve to fully closed and confirm smooth valve operation during closure and that the required force to close the valve is not excessive |  |  |  |  |
| 8 | Verify the direction of rotation to close |  |  |  | Direction of rotation to close: Anti-clockwise Clockwise |
| 9 | Count the number of turns between fully open and fully closed |  |  |  | Number of turns: ________________ |
| 10 | Confirm that the valve closed position indication is correct when in the fully closed position |  |  |  | Note gearbox end-stops may need adjustment if valve does not fully close |
| ELECTRIC ACTUATOR (TO BE COMPLETED WITH COMPETENT ELECTRICAL PERSONNEL) (Complete if a separate valve PC is not being completed) |
| 11 | Confirm that the actuator is set up for correct direction of rotation to open and close the valve |  |  |  |  |
| 12 | Confirm the seat/unseating torque for the valve by opening and closing the valve using the actuator. |  |  |  | Note the maximum seat/unseat torque will be when the differential pressure across the valve is the greatest. Manufacturer will have published torques Seat/Unseat Torque (max): _________Nm |
| 13 | Verify that open and close travel limits have been set up and that selected travel limit types (position or torque) are suitable for the valve type, with travel limit settings set correctly |  |  |  | Travel limit type: Position Torque |
| 14 | Confirm that the maximum opening and closing torque limits have been set up correctly on the actuator. Torque limits will be based on max valve seating/unseating. |  |  |  |  |
| 15 | Ensure the torque limits do not exceed the maximum rated input torque for the valve gearbox |  |  |  | Gearbox maximum rated input torque: _______________Nm |
| 16 | Confirm that actuator position (% open) is correct during operation |  |  |  |  |
| 17 | Verify that the actuator operates with uniform speed between 0% - 100% open |  |  |  |  |
| 18 | Check that travel limit switches operate correctly |  |  |  | The travel limit switches should be activated before the valve reaches gearbox end-stops to avoid actuator motor overload. The end-stops may require backing off . |
| 19 | Confirm that opening and closing running torques, breakout/unseat torques and seating torques are not excessive and the valve operates smoothly |  |  |  |  |
| 20 | Verify opening and closing times are correct for valve type and size |  |  |  | Opening / closing times: ___________ |

| 6. REMARKS / REMEDIAL / FOLLOW UP ACTIONS | ACTION BY | TARGET DATE | STATUS |
| --- | --- | --- | --- |

| 7. SIGNOFFS |
| --- |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |

APPENDIX A – SITE SPECIFIC PRE-REQUISITES

| A1. MECHANICAL PRE-REQUISITES | DONE | NO | ITR / DOCUMENT REF. |
| --- | --- | --- | --- |
|  |  |  |  | ITR-SV-M-AERATOR GWTP |
|  |  |  |  | ITR-CV-M-AERATOR GWTP |
|  |  |  |  | I-ACTUATOR-ELECTRO/MECHANICAL-SV-R |
|  |  |  |  | I-ACTUATOR-CV-R |
|  |  |  |  | I-ACTUATOR-PC-R |

APPENDIX A – SITE SPECIFIC PRE-REQUISITES (cont’d)

| A2. ELECTRICAL PRE-REQUISITES | DONE | NO | ITR / DOCUMENT REF. |
| --- | --- | --- | --- |