1. GENERAL DATA

PROJECT NAME:

PROJECT NO.:

WC P.O. / CONTRACT NO.:

| 2. EQUIPMENT DATA |
| --- |
| EQUIPMENT TITLE: | LOCATION: |
| MAKE: | MODEL: |
| TYPE: | WC DWG NO: |
| SERIAL NO: |  |

| 3. INSTALLATION CHECK | YES | NO | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- |
| 1 | Rotation Test (Trial Run) Liaise with Electrical Engineer to ensure that for the trail running the overloads and current sensors are set to high values to prevent spurious tripping. Ensure all guards are in place and it is safe to run. Check rotation direction. |  |  |  |  |
| 2 | Test rotate the Screen. Test Emergency stop. Rotate the screen one full revolution. |  |  |  |  |
| 3 | Check chain tension – adjust if required. Headshaft must be horizontal after chain adjustment. Record dimension from horizontal set point to head shaft centre lines for both chains. |  |  |  |  |
| 4 | Run current, forward; value |  |  |  |  |
| 5 | Check for smooth operation of equipment, check torque arm fixings. Forward direction Reverse direction |  |  |  |  |
| 6 | Check panel sealing rubbers |  |  |  |  |
| 7 | Check and make any final adjustments on current sensors/overloads (by others) |  |  |  |  |
| 8 | Check that drive unit does not over heat |  |  |  |  |
| 9 | Check that there are no oil leaks |  |  |  |  |
| 10 | Check that all hand/electrical operated valves are functioning correctly |  |  |  |  |
| 11 | Check spray bars are correctly set to clean efficiently (if w/w is available) |  |  |  |  |
| 12 | Set washwater spray pressure and flow rate and record Pressure: Flow: |  |  |  |  |
| 13 | Check pipe work for any visible leaks |  |  |  |  |
| 14 | Check ultrasonic heads are sited correctly relative to position of screen in channel. See TSE Drawing |  |  |  |  |
| 15 | Check ultrasonic heads are initially set to correct differential water levels and record Theoretical Setting: In flow to Screen: Out flow from Screen: |  |  |  |  |
| 16 | Check “high level” flow sensor is set to correct level (by others) and record Theoretical Setting: |  |  |  |  |
| 17 | Check guard/cover switches operate correctly |  |  |  |  |
| 18 | Set timer for closedown sequence (by others) to specified sequence interlock with screenings handling equipment. Screen to stop (mins in advance of screenings handling equipment) Screen washwater to stop (mins in advance of screenings handling equipment) |  |  |  |  |

| 4. COMMISSIONING CHECK | YES | NO | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- |
| 1 | Check screen under flow conditions for correct operation, and make any final adjustments where necessary |  |  |  |  |
| 2 | Check Spray pattern is effective in cleaning panels |  |  |  |  |
| 3 | Record M/C full screen load motor current |  |  |  |  |
| 4 | Check and record flow differential for single or two speed operation. Differential Levels – Start/low speed where applicable Start/high speed Alarm Change to slow speed Stop |  |  |  |  |
| 5 | Adjust ‘high level’ flow sensor as required and record actual setting |  |  |  |  |

5. REMARKS / REMEDIAL ACTIONS

| 6. SIGNOFFS |  |
| --- | --- |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |