A) INTRODUCTION

The following procedure is intended to ensure that the quality of procured product and its associated activities are completed by competent persons and:

- Comply with current and applicable specified requirements (including Corporation specifications / contract terms and conditions, national / international standards, manufacturer’s recommendations and industry best practices.

- Are conducted in a safe and professional manner.

- Provide an audit trail for verification of Quality Assurance and Quality Control compliance.

This procedure is for groundwater treatment plant THICKENERS & CLARIFIERS. Competent personnel shall complete all inspection / construction activities and record all activities on Water Corporation Document (ITP-CV-M-THICKENERS & CLARIFIERS); for each asset inspected. Note a supply verification SV has not been prepared as most thickeners and clarifier are constructed on site rather than being preassembled.

NOTE:

- Please ensure that all ITP documents are completed by a competent person and that all Water Corporation SAFETY and operational requirements are to be complied with at all times in relation with Water Corporation and Australian Standards where applicable.

B) COMPLETED DOCUMENTS

Completed documents are to be scanned and saved as a .pdf file in the relevant AQUA folder utilising the following naming convention:

LOCATION - DISCIPLINE - ASSET – ASSET TYPE – VENDOR NAME – DOCUMENT TYPE – P&ID TAG – REVISION NUMBER

E.g. RavenswoodPS_M_Valve_Butterfly_Tyco_SV_1000BV3422_1

The commissioning manager shall coordinate incorporation of completed ITPs in conjunction with the CAMEL.

Feedback on improvements to ITPs should be directed to MESB Mechanical for incorporation into future versions.

| 1. REFERENCE INFORMATION |
| --- |
| INSPECTION DATA | ASSET DATA |
| PROJECT NAME: | MANUFACTURER: |
| LOCATION: | MF SERIAL NO: |
| INSPECTION DATE: | WC FLER / TAG NO: |
| INSPECTOR NAME: | TYPE / MODEL NO / SIZE: |
| PROJECT / CONTRACT NO: | DESIGN CRITERIA: |
| ATTENDEES: |

| 2. INSPECTION PREPARATION |
| --- |
|  | OSH compliance requirements. |
|  | Obtain QA / QC documentation (review outstanding items). |
|  | Relevant Water Corporation standards. |
|  | Relevant Australian Standards. |
|  | Supporting contract documentation / approved drawings. |
|  | Provision of required test equipment. |
|  | Provision of required test reports and certificates; i.e. hydrostatic test, material certificates, etc. |

*Contents of Section 3 (Inspection) and Section 4 (Test) are Asset Specific and shall reflect relevant SPS / Australian Standard(s) where practicable. Entries shall also be worded to reflect the procedures involved in a step-by-step manner; i.e. “Conduct visual inspection and ensure pre-start photographs are taken”, “Extract bearing housing covers to expose bearings and full shaft length”.

| 3. INSPECTION | YES | NO | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- |
| GENERAL |
| 1 | Locate and verify that name plate/label details match specification and contract requirements |  |  |  | Check: Design Code/Volume Capacity/Internal Diameter / Flow Capacity/Year of Manufacture /Side Water depth/Freeboard |
| 2 | Confirm if O&M Manuals have been provided (hardcopy / softcopy) |  |  |  | Hardcopy / softcopy? (please circle) |
| MATERIALS AND ARRANGEMENT |
| 3 | Verify construction materials with material certificates, specification and relevant drawings |  |  |  |  |
| 4 | Confirm materials of construction (especially for ladders, stairways, access platforms) meet DS 30-02 requirements according to chemicals stored |  |  |  |  |
| 5 | Confirm major dimensions correct per drawing |  |  |  | Attach a copy of the clarifer drawing to this record sheet highlighting on the drawing which dimensions were checked. |
|  | Influent Pipe Connection |  |  |  |  |
| 6 | - Flange standard correct? |  |  |  | Flange face: FF / RF |
| 7 | - Diameter correct? |  |  |  | Class: |
| 8 | - Pitch circle diameter correct? |  |  |  | PCD: _____________ mm |
| 9 | - Number and diameter of bolt holes correct? |  |  |  | No.:__________ Dia.:__________ mm |
|  | Effluent /Launder Pipe Connection |  |  |  |  |
| 10 | - Flange standard correct? |  |  |  | Flange face: FF / RF |
| 11 | - Diameter correct? |  |  |  | Class: |
| 12 | - Pitch circle diameter correct? |  |  |  | PCD: _____________ mm |
| 13 | - Number and diameter of bolt holes correct? |  |  |  | No.:__________ Dia.:__________ mm |
|  | Rake or Sludge Collector Arm Assembly |  |  |  |  |
|  | Rakes |  |  |  |  |
| 14 | Confirm tie-rods and struts fitted |  |  |  |  |
| 15 | Check hydrotest ports plugged |  |  |  |  |
| 16 | Confirm underflow scraper fitted |  |  |  |  |
| 17 | Check bed mass snout is clear |  |  |  |  |
| 18 | Confirm adequate clearances in fully raised/lowered position |  |  |  |  |
| 19 | Check rakes will scrape to centre |  |  |  | (clockwise looking from top) |
|  | Steady Bearing or Guide Pin |  |  |  |  |
| 20 | Check is centralised and has no preload |  |  |  |  |
| 21 | Confirm bearing components fitted |  |  |  |  |
| 22 | Check bearing post is correct height |  |  |  |  |
| 23 | Confirm underflow cone area is clean |  |  |  |  |
| 24 | Confirm correct grade of bolts have been used |  |  |  |  |
|  | Guide Blocks |  |  |  |  |
| 25 | Confirm blocks are shimmed to correct height? |  |  |  |  |
| 26 | Confirm blocks have nipples installed and greased? |  |  |  |  |
| 27 | Confirm blocks are securely fastened to correct bolt torques? |  |  |  | Bolt Torques …………Nm |
| 28 | Confirm blocks are fitted in correct position and height? |  |  |  |  |
|  | Rakelift Cylinders |  |  |  |  |
| 29 | Check cylinder clevis pins and clips fitted |  |  |  |  |
| 30 | Check cylinder fittings are accessible and secure |  |  |  |  |
| 31 | Confirm hydraulic hose fittings to cylinders are tight and free of defects |  |  |  |  |
| 32 | Confirm hydraulic hoses are of sufficient length to accommodate rake lift |  |  |  |  |
|  | Rakelift Guards |  |  |  |  |
| 33 | Confirm guards fit correctly in position and are complete and free of defects |  |  |  |  |
|  | Rakelift Limits |  |  |  |  |
| 34 | Ensure limit switches are set at correct position |  |  |  |  |
| 35 | Confirm bracket/bolts fitted |  |  |  |  |
| 36 | Check striker tabs work correctly |  |  |  |  |
| 37 | Target plate fitted and area clear of obstruction |  |  |  |  |
|  | Hydraulic Powerpack for Rakelift |  |  |  |  |
| 39 | Confirm hydraulic oil is filled to correct static level |  |  |  |  |
| 40 | Confirm drive shut-off valve is fitted |  |  |  |  |
| 41 | Check motor wired correctly for correct direction of rotation |  |  |  |  |
|  | Rotating Drum |  |  |  |  |
| 42 | Check there is adequate clearance between recirculating drum and rotating drum |  |  |  |  |
|  | Drive Assembly |  |  |  |  |
|  | Electric Motor and Gearbox |  |  |  |  |
| 43 | Confirm hold down bolts are tightened to correct torques |  |  |  | Bolt Torques …………Nm |
| 44 | Check that all plugs are fitted and tight |  |  |  |  |
| 45 | Confirm gearbox oil level is adequate |  |  |  |  |
| 46 | Confirm correctly sized oil fill canister has been installed |  |  |  |  |
| 47 | Check oil canister is at correct height |  |  |  |  |
| 48 | Has an oil low level switch been installed? |  |  |  |  |
| 49 | For direct coupled motor confirm gasketing has been installed on flange mount |  |  |  |  |
| 50 | Confirm gearbox case drain valve and hose installed |  |  |  |  |
| 51 | Confirm gearbox vent/breather has been installed |  |  |  |  |
|  | Slew Bearing Assembly |  |  |  |  |
| 52 | Check grease nipples and lines have been installed |  |  |  |  |
| 53 | Confirm bearing is adequately greased |  |  |  |  |
|  | Drive Pinion |  |  |  |  |
| 54 | Check level indicator fitted |  |  |  |  |
| 55 | Confirm oil level is adequate |  |  |  |  |
| 56 | Check for inadvertent water ingress |  |  |  |  |
| 57 | Check all inspection hatches fitted |  |  |  |  |
|  | Drive Coupling |  |  |  |  |
| 58 | Confirm correct bolts are used and torque applied meets manufacturer’s specification |  |  |  |  |
| 59 | Check alignment meets tolerances |  |  |  |  |
| 60 | Confirm all items are cleared during lift cycle |  |  |  |  |
| 61 | Confirm rake position indicators are operational |  |  |  |  |
|  | Structural |  |  |  |  |
|  | Bridge Support Structure |  |  |  |  |
| 62 | Measure precamber on left and right beam and confirm compliance with drawings |  |  |  | Left Beam …………..mm Right Beam …………mm |
| 63 | Verify access walkway meets WC and AS standards in relation handrails, gridmeshing, widths etc |  |  |  |  |
| 64 | External access stairs to AS1657 and S151? |  |  |  |  |
|  | Tank Walls/ Floor |  |  |  |  |
| 65 | Check orientation of bridge/overflow/exit against drawings |  |  |  |  |
| 66 | Confirm bolts are tensioned correctly |  |  |  |  |
| 67 | Ensure splice joint is complete and tensioned correctly |  |  |  |  |
| 68 | Ensure all tank welds are inspected and meet WS-1 requirements |  |  |  |  |
| 69 | Confirm all bay bracing is complete to manufacturer’s drawings |  |  |  |  |
| 70 | Ensure inner floor gore/cone infill plates are installed |  |  |  |  |
| 71 | Confirm monorail (if applicable) has safe working load (SWL) displayed |  |  |  |  |
| 72 | Check internal and external protective coating or lining is to manufacturers specification |  |  |  |  |
|  | Reaction/Feed Well |  |  |  |  |
| 73 | Check deflector cone/reaction well gap is to specification |  |  |  |  |
| 74 | Confirm correct number and arrangement of baffle plates |  |  |  |  |
| 75 | Check influent feed pipe is supported adequately |  |  |  |  |
| 76 | Confirm lining meets manufacturer’s specification |  |  |  |  |
| 77 | For “autodilution” fitted clarifiers confirm these are of correct number, height and size |  |  |  | Note supernatant is at time used to dilute influent solids level using pressure differentials |
| 78 | For “turbodilution” fitted clarifiers confirm these are fitted correctly to manufacturer’s drawings and specification |  |  |  | Note supernatant is at time used to dilute influent solids level using external pump |
| 79 | Ensure hanger rods are securely fastened to reaction well and bridge beam and turnbuckles are adequately tensioned |  |  |  |  |
|  | Launders |  |  |  |  |
| 80 | Confirm central radial launder is securely fastened to reaction well |  |  |  |  |
| 81 | Confirm radial launders are secure attached to clarifier wall and radial launder |  |  |  |  |
| 82 | Check launder orifices are located at correct height relative to intended top of water level (TWL) |  |  |  |  |
|  | Chemical Dosing |  |  |  |  |
| 83 | Ensure chemical dosing pipework is of correct size and material of construction |  |  |  |  |
| 84 | Confirm pipework is securely fastened and supprted and it’s discharge point is in correct location |  |  |  |  |
|  | Sludge Thickening Underflow |  |  |  |  |
| 85 | Check sludge withdrawal pipe is of correct size |  |  |  |  |
| 86 | Ensure adequate clearance between cone scraper and solids thickening trough |  |  |  |  |
| 87 | Confirm bolts are of correct size, grade and tension between toque shaft and cone scraper |  |  |  |  |

| 4. TEST | PASS | FAIL | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- |
| 1 | Not applicable |  |  |  |  |

*Contents of Section 5 to be retained where applicable; i.e. if coatings inspection is required. Sections 6-9 to be retained in all ITPs.

| 5. COATINGS INSPECTION (Applicable for external and internally coated clarifiers & thickeners) | YES | NO | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- |
| 1 | Verified construction materials with specification and relevant drawings |  |  |  | Substrate material: |
| 2 | Review surface pre-treatment and/or preparation procedure (circle PH: Epoxy Coating on Steel/Cast Iron or state Other) |  |  |  | PA / OTHER _________________ |
| 3 | Verify coating system and specification ensuring that product is approved for purpose |  |  |  |  |
| 4 | Ensure that surface preparation was acceptable and free from contaminants prior to coating/complies to spec Consider dust and spent abrasive, oil and contamination, flash rusting, slag, porosity, weld spatter, sharp edges, free from laminations, free from burrs etc |  |  |  | Class of surface finish (if known): Profile (if known): Coating application (if known): |
| 5 | Consider if conditions acceptable for testing. Surface temperature should be least 3ºC above dew point and relative humidity less than 85 % before testing |  |  |  | Conditions: |
| 6 | Fully cured coating system should be adherent while in their service condition (Method AS/NZS 3894.9) |  |  |  | Failure force (if known): |
| 7 | Assess degree of cure and hardness of coating is acceptable (method AS 3894.4). Allow sufficient drying and curing of the coating prior conducting testing. The length of time shall be obtained from the coating manufacture. |  |  |  | Method used: |
| 8 | Visually inspect surfaces and ensure is adequately clean and dry prior to testing |  |  |  | Method/chemicals used: |
| 9 | Check internal coating type and verify in accordance with relevant specification (circle PH: Epoxy Coating on Steel/Cast Iron or state, PA: Protective Coating on Steel/Cast Iron or state Other) |  |  |  | PA / PH / OTHER _____________ |
| 10 | Visually inspect condition of internal coating appearance including uniformity, colour and free from any defect that could impair performance and/or appearance of coating. |  |  |  |  |
| 11 | Check external coating type and verify in accordance with relevant specification (circle PH: Epoxy Coating on Steel/Cast Iron or state, PA: Protective Coating on Steel/Cast Iron or state, PS: Inorganic zinc silicate primed two pack acrylic coating or Other ) |  |  |  | PA / PH / PS/ OTHER _____________ |
| 12 | Visually inspect condition of external coating appearance including uniformity, colour and free from any defect that could impair performance and/or appearance of coating. |  |  |  |  |
| 13 | Calibrate thickness tester to standard of uniform and calibrated thickness, covering appropriate range of film thicknesses to be measured |  |  |  | Method/instrument used: |
| 14 | Visually inspect and measure dry film thickness (DFT) in at least 10 locations on coated surfaces. Record values, ensure compliance with spec and record in table below |
| 15 | Ensure coating fully cured prior continuity testing by checking datasheet for required time to full cure or other appropriate test method |  |  |  | Temp/time: Test method: |
| 16 | Calibrate holiday detector (spark tester) electrode with appropriate volt meter which has been laboratory calibrated within the last 2 years to proposed voltage. Record brand and model of spark tester to be used. |  |  |  | Brand/model used: |
| 17 | Carry out spark test on internal coating in accordance to AS/NZS 3894.1 Continuity testing of non-conductive coating – High Voltage (brush) method. Specify voltage at which test is carried out. |  |  |  | Test Voltage: V |
| 18 | Carry out spark test on external coating accordance to AS/NZS 3894.1 Continuity testing of non-conductive coating – High Voltage (brush) method. Specify voltage at which test is carried out. |  |  |  | Test Voltage: V |
| 19 | Asset passes continuity testing with zero defects (including pinholes, holidays, cracks and other discontinuities) detected in finished coating for immersed conditions and/or subsequent repairs have been carried out before being placed in service. |  |  |  |  |

| Coating Thickness: | Internal (micrometers): | External (micrometers): | Flange (micrometers ): | Complies with Spec? |
| --- | --- | --- | --- | --- |
| Specified min |  |  |  | N/A |
| Specified max |  |  |  | N/A |
| Measured 1 |  |  |  |  |
| Measured 2 |  |  |  |  |
| Measured 3 |  |  |  |  |
| Measured 4 |  |  |  |  |
| Measured 5 |  |  |  |  |
| Measured 6 |  |  |  |  |
| Measured 7 |  |  |  |  |
| Measured 8 |  |  |  |  |
| Measured 9 |  |  |  |  |
| Measured 10 |  |  |  |  |
| Average |  |  |  |  |
| Note any comment or variation to test procedure that will assist in interpretation of results: |

Refer to AS/NZS 1627 series for Metal Finishing – Preparation and Pretreatment of Surfaces

2 Refer to AS/NZS 3894.7 for practical procedure for Determination of Surface Temperature of metal surfaced (pre-coating)

3 Refer to AS/NZS 3894.3 methods for Determination of Dry Film Thickness

4 Method AS 3894.3 refers Determination of Dry Film Thickness

| 6. REMARKS / REMEDIAL / FOLLOW UP ACTIONS | ACTION BY | TARGET DATE | STATUS |
| --- | --- | --- | --- |

| 7. SIGNOFFS |
| --- |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |

# Footnotes

Refer to AS/NZS 1627 series for Metal Finishing – Preparation and Pretreatment of Surfaces

Refer to AS/NZS 3894.7 for practical procedure for Determination of Surface Temperature of metal surfaced (pre-coating)

Refer to AS/NZS 3894.3 methods for Determination of Dry Film Thickness

Method AS 3894.3 refers Determination of Dry Film Thickness