## ITP - GRP PV Manufacture
INSPECTION AND TEST PLAN GRP / FRP Pressure Vessel - Manufacture | [8 empty] | [& Contractor Logo]
Project Number: |  |  | Project Name: | [5 empty] | H | Hold Point | V | Verification Point
Contract Number: |  |  | ITP No: |  | Rev: |  |  |  | W | Witness Point | S | Surveillance Point
Issue Date: Drafted by: Approved by: |  |  | Manufacturer: |  | Design Criteria: |  |  |  | Refer to end of ITP for notes on each of the points.
Description: |  |  |  |  | MF Serial No.:
Item No. | Description | Acceptance Criteria | Frequency | Deliverable/Verification Documentation | MDR / Quality Record | Manufacturer Responsibility |  |  | Customer Resp - QA/QC | Client / End User Resp - QA/QC | Water Corporation | Comments
[6 empty] | Management | Production | QC
1 | Project Review
1 | Review Contract Documents
1.01 | Design review and specification verification/ Raw material procurement | Design code and project specification requirements BS EN13121-3 | Prior to issue of manufacturing drawings and commencement of manufacture | Calculation documentation | Include | Hold | Hold | Hold |  | verify | verify
1.02 | Drawing Review / Submit shop drawings for approval | Specification and Project standards | At the start of the project | Drawings | Include | Hold | Hold | Verify |  | verify | verify
1.03 | Preparation and submission of ITP for approval | Specification requirements | Prior to commencement of manufacture | Completed ITP & Deliverable documents |  | Verify | Verify | Hold |  | verify | verify
1.04 | Prepare QA Documentation / check and issue shop drawings / work instructions / kick off meeting etc | Specification requirements- together with in-house quality management documentation | Prior to commencement of manufacture | Quality and design pack for approval/ review | Include ITP and relevant deliverable docs | Verify | Verify | Hold |  | verify | verify
2 | Incoming Raw Materials Inspection
2.0 | Resins | Manufacturers data sheets/ PO Spec requirements / in accordance with AS 4020 for use in contact with potable water | Each delivery and or batch number | Supplier's Certificate of Compliance and Analysts Doc | Include Certs | Verify | Verify | verify |  |  | verify
2.01 | Traceability/ batch Nos, | Purchase Order and data sheets | Each Delivery lot/ drum | In house receiving documentation |  | Verify | Verify | verify
2.02 | Gel Time | Resin Data sheets | 1 sample from each Batch | In House Gel time record sheet Supplier's Certificate of Compliance and Analysts Doc |  | Verify | Verify | verify
2.03 | Barcol hardness on each resin casting | Not less than 80% of resin manufacturers value | 1 sample from each Batch | Gel Time test record |  | Verify | Verify | verify
2.1 | Glass Fibre | Manufacturers data sheets/ PO Spec requirements / in accordance with AS 4020 for use in contact with potable water | Each delivery and or batch number | Supplier's Certificate of Compliance and Analysts Doc | Include Certs | Verify | Verify | verify |  |  | verify
2.11 | Pallet Inspection | Appearance/ check for water damage | Each pallet/ lot | In house receiving documentation |  | Verify | Verify | Surveillance
2.12 | Traceability/identification/ batch No. | Purchase Order and data sheets | Each pallet/ lot | In house receiving documentation |  | Verify | Verify | verify
2.2 | Catalyst | Manufacturers data sheets/ PO Spec requirements / in accordance with AS 4020 for use in contact with potable water | Each delivery and or batch number | Supplier's Certificate of Compliance and Analysts Doc | Include Certs | Verify | Verify | verify |  |  | verify
2.21 | Traceability/ batch No, | Purchase Order and data sheets | Each pallet/ lot | In house receiving documentation |  | Verify | Verify | verify
2.22 | Check shelf life/ date on manufacture | Data sheets | Each delivery and or batch number | In house receiving documentation |  | Verify | Verify | verify
2.23 | Reactivity/ Gel time consistency | Production requirements | 1 sample from each Batch | Test report/Supplier's Certificate of Compliance and Analysts Doc |  | Verify | Verify | verify
2.3 | Additives | Manufacturers data sheets/ PO Spec requirements / in accordance with AS 4020 for use in contact with potable water | Each delivery and or batch number | Supplier's Certificate of Compliance and Analysts Doc | Include Certs | Verify | Verify | verify |  |  | verify
2.31 | Traceability/identification/ batch No. | Purchase Order and data sheets | Each Delivery/Batch | In house receiving documentation |  | Verify | Verify | verify
2.32 | Visual Inspection/ Shelf life /expiry date | Manufacturers data sheets/ Spec requirements | Each delivery /pallet/ lot | In house receiving documentation |  | Verify | Verify | verify
3 | Component Production and Routine Testing
3.1 | Validation of laminator approval certification | BS EN13121-3 | 1 test for each laminator valued for 5 years provided it can be shown that the laminator has been employed with reasonable continuity of work. | Laminator approval test certificate No. WFE001-15, WFE002-15…..WFE012-15 |  | Verify | Verify | Verify
3.2 | Suitable condition of works and storage of raw materials | BS EN13121-3 raw materials supplier requirements | Prior to startup and ongoing | Warehouse Material Storage Temperature & Humidity |  | Verify | Surveillance | Surveillance |  |  |  | Record of Warehouse material storage temperature & humidity
3.3 | Record Temperature and Dew point /humidity of work area | BS EN13121-3 minus Min 10°C No less than 3 degrees of Dew point Ref 15.2.4 No work at dew point | Minimum of 2 times a shift | Temperature / Dew Point / Humidity Record. Doc. Control no: WFE/PF/FRM/021/Rev00 |  | Verify | Surveillance | Verify |  |  |  | Record of temperature & dew point at Production
3.4 | Tooling/ mould dimensions/ visuals/ release agent | Specification requirements / design validation | At beginning of production/ each tool, equipment | Product Manufacturing Record. Doc. Control no: WFE/PF/FRM/020/Rev00 | include | Verify | Surveillance | Verify |  |  |  | Tooling / Mould Dimension record
3.5 | Application of internal Chemical barrier | Design Specification to BS EN13121-3 | Each component/vessel | Product Manufacturing Record. Doc. Control no: WFE/PF/FRM/020/Rev00 | Include | Verify | Surveillance | Surveillance
3.6 | Application of structural layers/correct resin, glass and cure system | Design Specification to BS EN13121-3 | Each component/vessel | Product Manufacturing Record. Doc. Control no: WFE/PF/FRM/020/Rev00 | Include | Verify | Surveillance | Verify
3.7 | Record materials/ batch numbers | Specification/works instructions | Each component | Product Manufacturing Record. Doc. Control no: WFE/PF/FRM/020/Rev00 | Include | Verify | Surveillance | Verify |  |  |  | Product Manufacturing Record
3.8 | Inner shell structure preparation /correct jointing laminate | Specification/ drawings/ minimum tapers 1:6 | Each component | Product Manufacturing Record. Doc. Control no: WFE/PF/FRM/020/Rev00 | Include | Verify | Surveillance | Verify |  |  |  | Product Manufacturing Record
3.9 | Dimensional & tolerance, orientations, elevations, squareness, parallelism, thickness O ring groove, flange flatness, support ring true, nozzle orientation and all dimensions indicated in the drawing and the control sheet. | Specification, Drawings BS EN13121-3 tolerances/SPS 250. | Each component | Marked up as- built drawings and check sheets | Include | Verify | Surveillance | Surveillance |  |  |  | MDR
3.10 | Nozzle internal overlay construction laminate plies and thickness check. | Specification, Drawings BS EN13121-3 tolerances | Each nozzle | Marked up as- built drawings and check sheets | Include | Verify | Surveillance | Hold |  | Surveillance
3.11 | Barcol Hardness, | 80% of resin manuf checked per BS EN13121-3 | Each component | Manufacturer's Data Report Control no: WFE/EN/FRM/018/Rev00 | Include | Verify | Verify | Hold |  |  |  | MDR
3.12 | Post Cure | SPS250 | Each Vessel | Product Manufacturing Record. Doc. Control no: WFE/PF/FRM/020/Rev01 | Include | Verify | Verify | Hold |  |  |  | MDR
3.13 | Acetone Surface sensitivity of surfaces | Checked per BS EN13121-3 | Each component | Product Manufacturing Record. Doc. Control no: WFE/PF/FRM/020/Rev00 | Include | Verify | Hold | Surveillance |  |  |  | MDR
3.14 | Burnoff & Construction Analysis | Checked per BS EN13121-3 | Each Vessel major component i.e. Heads and shells | Product Manufacturing Record. Doc. Control no: WFE/PF/FRM/020/Rev00 | Include | Verify | Hold | Hold |  | Verify |  | Verification of Laminating Records
3.15 | Hydrostatic pressure test of vessel in accordance with BS EN13121-3 / SPS 250. | 1.3 times design pressure for a minimum of 1 hour. | Each vessel | Product Manufacturing Record. Doc. Control no: WFE/PF/FRM/020/Rev00 | Include | Verify | Witness | Witness |  | Witness |  | MDR
3.16 | Appearance/ visual defects/ cracks after hydrotest | Specification / Visual defects BS EN13121-3 | Each component | Product Manufacturing Record. Doc. Control no: WFE/PF/FRM/020/Rev00 | Include | Verify | Surveillance | Surveillance |  | Surveillance |  | MDR
3.17 | Application of exterior top coat/ correct resin , wax and cure system after 3rd party inspection | Specification/ drawing | Each vessel | Specification/ drawing | Include | Verify | Surveillance | Surveillance |  |  |  | MDR
4 | Final Inspection
4.1 | Identification and Marking | Specification/ drawings item numbers/Statutory requirements minimum requirements of BS EN13121-3 | Each vessel | BS EN13121-3 and AS 1210 Requirements | Include Photostat copy of name plate/label | Verify | Surveillance | Surveillance |  |  |  | MDR
4.2 | Final dimensional / visual checks for compliance including all internals, attachments and accessories. | Specification/ contract requirements BS EN13121-3 / SPS 250 table 5.1 | Each vessel | Drawings / specification | Include | Verify | Hold | Hold |  |  |  | MDR
4.3 | Prepare Certificate of compliance & delivery note/ shipping docs | Specification/ contract requirements | Each Delivery | Certificate No. 13952-COC in accordance with Spec and EN 10204:2004 2.1 or 3.1 |  | Verify | Verify | Hold |  |  |  | Certificate of Compliance
4.4 | Release note submission by customer and client and receipt of acceptance | Project requirement and format | Each Delivery | Release No. xxxx signed by Client | Include | Verify | Verify | Verify |  |  |  | From customer
4.5 | Security of Load, Protection and packaging | Logistics Pack. Specific specification requirements | Each batch / delivery | Dispatch documents/ Packing list | Include | Verify | Surveillance | Surveillance |  |  |  | Packing List
5 | MDR
5.1 | Prepare MDR with all requirements | Per Contract Requirement | Per Decanter / contract requirement | MDR as per ITP and customer requirements | Complete and submit | Verify | Verify | Hold |  |  |  | MDR
Sign Off
Manufacturer Approval |  |  | Third Party Approval |  | Customer Representative Approval |  |  |  | Water Corporation Approval
Name: |  |  | Name: |  | Name: |  |  |  | Name:
Position: |  |  | Position: |  | Position: |  |  |  | Position:
Date: |  |  | Date: |  | Date: |  |  |  | Date:
Note:
o Hold Points (H): |  | A step in design, fabrication, installation, construction, testing or maintenance beyond which the process may not proceed without checking, inspection and authorization by the authority who imposed the hold point.
o Witness Point (W): |  | A step in design, fabrication, installation, construction, testing or maintenance where the authority who imposed the witness point performs an inspection or surveillance.
If such inspection or surveillance is not performed at the agreed time, after proper notification that the witness point will occur, or if such inspection is waived, processing may continue.
o Verification Point (V): |  | A step in design, fabrication, installation, construction, testing or maintenance where the authority who imposed the verification point reviews documentation applicable to the surveillance point to ensure correction compilation and acceptability of such documentation.
o Surveillance Point (S): |  | A step in design, fabrication, installation, construction, testing or maintenance were the authority who imposed the surveillance point is notified in advance of the activity to enable him to visit the location of the activity
if required to conduct a general surveillance without delaying the activity.