| - All ITR documents to be completed & witnessed by competent person/s - Compliance to be achieved to contract requirements and all latest versions of applicable standards |  |
| --- | --- |
| 1. REFERENCE INFORMATION |  |
| INSPECTION DATA | ASSET DATA |
| PROJECT NAME: | MANUFACTURER: |
| LOCATION: | MF SERIAL NO: |
| INSPECTION DATE: | WC FLER / TAG NO: |
| INSPECTOR NAME: | TYPE / MODEL NO / SIZE: |
| PROJECT / CONTRACT NO: | DESIGN CRITERIA: |
| ATTENDEES: |  |

| 2. INSPECTION PREPARATION |  |
| --- | --- |
|  | OSH compliance requirements. |
|  | Obtain QA / QC documentation (review outstanding items). |
|  | Relevant Water Corporation standards. |
|  | Relevant Australian Standards. |
|  | Supporting contract documentation / approved drawings. |
|  | Provision of required test equipment (portable vibration monitor and temperature sensor). |
|  | Provision of required test reports and certificates |
|  | Provision of completed construction verification |

| 3. INSPECTION PRELIMINARIES |  | YES | NO | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- | --- |
| VESSEL DATA |  |  |  |  |  |
| 1 | Design pressure? |  |  |  | kPa |
| 2 | Max number of pressure cycles? |  |  |  | cycles |
| 3 | Design temperature |  |  |  | °C |
| 4 | Minimum Operating temperature |  |  |  | °C |
| 5 | Design Registration number? |  |  |  |  |
| 6 | Hazard Level rating ? (AS 4343) |  |  |  |  |
| 7 | Maximum working pressure of vessel? |  |  |  | kPa |
| 8 | Hydrostatic Test Pressure? |  |  |  | kPa |
| PRE-START |  |  |  |  |  |
| 9 | “Punchlist” reviewed and free of significant defects preventing asset pre-commissioning? |  |  |  |  |
| 10 | Hazard identification and risk assessment for asset pre-commissioning complete? |  |  |  |  |
| 11 | Electrical construction and pre-commissioning ITPs complete? |  |  |  |  |
| 12 | Mechanical and electrical site specific pre-requisite ITPs complete? (Refer Appendix A) |  |  |  |  |

*Contents of Section 4 (Inspection) and Section 5 (Test) are Asset Specific and shall reflect relevant SPS / Australian Standard(s) where practicable. Entries shall also be worded to reflect the procedures involved in a step-by-step manner; i.e. “Conduct visual inspection and ensure pre-start photographs are taken”, “Remove bearing housing covers to expose bearings and full shaft length”.

| 4. INSPECTION |  | YES | NO | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- | --- |
| 1. | Inspect the interior of the filter vessel(s) for any damage. |  |  |  |  |
| 2. | Has any large debris or particulates internal of the vessel been removed? |  |  |  | Undertake by vacuuming or wiping. Care should be taken if entry into the vessel is required. All necessary procedures and permits shall be adhered to. |
| 3. | Has clean water been used to rinse out the internals of the vessel of smaller particulates through the low point drain port? |  |  |  |  |
| 4 | Has the required media been filled up to the recommended level? |  |  |  |  |
| 5 | Check the Air Relief valve flow path is clear and unrestricted, any isolation valves are open |  |  |  |  |
| 6 | Check the Pressure Relief valve flow path is clear and unrestricted |  |  |  | No isolation valve is allowed between vessel and relief valve |

| 5. TEST |  | YES | NO | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- | --- |
| HALF MAXIMUM VOLUME CAPACITY TEST |  |  |  |  |  |
| 1 | Water level correct for start of leak testing? |  |  |  | Water level: ________________ m |
| 2 | Half working volume leak test conducted at correct level? |  |  |  | Level: ____________________ m |
| 3 | All nozzles, man holes and tapping points hydraulically tight (no leaks)? |  |  |  |  |
| 4 | Confirm construction joins are leak free? |  |  |  |  |
| THREE-QUARTERS MAXIMUM VOLUME CAPACITY TEST |  |  |  |  |  |
| 5 | Three-quarters working volume leak test conducted at correct level? |  |  |  | Water Level: ______________ m |
| 6 | All nozzles, man holes and tapping points hydraulically tight (no leaks)? |  |  |  |  |
| 7 | Confirm construction joins are leak free? |  |  |  |  |
| FULL MAXIMUM VOLUME CAPACITY TEST |  |  |  |  |  |
| 8 | Full working volume leak test conducted at correct level? |  |  |  | Water Level: ______________ m |
| 9 | All nozzles, man holes and tapping points hydraulically tight (no leaks)? |  |  |  |  |
| 10 | Confirm construction joins are leak free? |  |  |  |  |
| FULL MAXIMUM WORKING PRESSURE TEST |  |  |  |  |  |
| 8 | Full working pressure leak test conducted at correct pressure? |  |  |  | Test pressure: ______________ kPa |
| 9 | All nozzles, man holes and tapping points hydraulically tight (no leaks)? |  |  |  |  |
| 11 | Confirm pressure monitoring is operational and reading is correct. |  |  |  |  |

| 6. REMARKS / REMEDIAL / FOLLOW UP ACTIONS | ACTION BY | TARGET DATE | STATUS |
| --- | --- | --- | --- |

| 7. SIGNOFFS |  |  |  |
| --- | --- | --- | --- |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |

APPENDIX A – SITE SPECIFIC PRE-REQUISITES

| A1. MECHANICAL PRE-REQUISITES |  | DONE | NO | ITR / DOCUMENT REF. |
| --- | --- | --- | --- | --- |
|  |  |  |  | ITP-SV-M-FRP MULTI-MEDIA PRESSURE VESSELS |
|  |  |  |  | ITP-CV-M-FRP MULTI-MEDIA PRESSURE VESSELS |

APPENDIX A – SITE SPECIFIC PRE-REQUISITES (cont’d)

| A2. ELECTRICAL PRE-REQUISITES |  | DONE | NO | ITR / DOCUMENT REF. |
| --- | --- | --- | --- | --- |