| All ITR documents to be completed & witnessed by competent person/s Compliance to be achieved to contract requirements and all latest versions of applicable standards |
| --- |
| 1. REFERENCE INFORMATION |
| INSPECTION DATA | ASSET DATA |
| PROJECT NAME: | MANUFACTURER: |
| LOCATION: | MF SERIAL NO: |
| INSPECTION DATE: | WC FLER / TAG NO: |
| INSPECTOR NAME: | TYPE / MODEL NO / SIZE: |
| PROJECT / CONTRACT NO: | DESIGN CRITERIA: |
| ATTENDEES: |

| 2. INSPECTION PREPARATION |
| --- |
|  | OSH compliance requirements. |
|  | Obtain QA / QC documentation (review outstanding items). |
|  | Relevant Water Corporation standards. |
|  | Relevant Australian Standards. |
|  | Supporting contract documentation / approved drawings. |
|  | Provision of required test equipment. |
|  | Provision of required test reports and certificates; i.e. hydrostatic test, material certificates, etc. |

*Contents of Section 3 (Inspection) and Section 4 (Test) are Asset Specific and shall reflect relevant SPS / Australian Standard(s) where practicable. Entries shall also be worded to reflect the procedures involved in a step-by-step manner; i.e. “Conduct visual inspection and ensure pre-start photographs are taken”, “Extract bearing housing covers to expose bearings and full shaft length”.

| 3. INSPECTION | YES | NO | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- |
| GENERAL |
| 1 | Locate and verify that name plate/label details match specification and contract requirements |  |  |  | Check: Make/Model/Connection size/Serial number/ Design Code/Volume/Internal Diameter / Operating Fluid/Design Pressure/Hazard level/Year of Manufacture etc |
| 2 | Design review and specification verification/ Raw material procurement |  |  |  | Manufacturing ITP. Design code and project specification requirements AS 1210 section 10 and/or BS EN13121-3. |
| 3 | Verify vessel design and construction as per “as constructed” drawing/s |  |  |  | Note: drawing number/s and revisions against MDR and design registration |
| 4 | Determine vessel is undamaged and free from contaminants |  |  |  |  |
| 5 | No exposed fibres and machined faces are free of sharp edges, burrs and defects? |  |  |  |  |
| 6 | Confirm receipt and completion of manufacturers data report (MDR) and that it has been audited by a competent person. |  |  |  | MDR should include: ITP, design registration certificate, material specifications, resins, glass fibre and catalysts, additives data sheets (see Materials and Arrangement), consumable certificates, determination of tensile strength, non-destructive testing and delivery dockets. Relief device data and test certificate/s. |
| 7 | Certificates of compliance with AS 1210 section 10 and/or EN13121-3 |  |  |  | Notice of compliance with ¹AS 1210 section 10 or certificate no. 13952-COC in accordance with Spec and EN 10204:2004 2.1 or 3.1 |
| 8 | Confirm if O&M Manuals have been provided (hardcopy / softcopy) |  |  |  | Hardcopy / softcopy? (please circle) |
| MATERIALS AND ARRANGEMENT |
| 9 | Verify construction materials with material certificates, specification and relevant drawings |  |  |  | Evidence from MDR, manufacturing ITP, drawings, material certificates and suppliers specifications sample reports. AS4020 (or equivalent) approved. |
| 10 | Resins – Data sheets, PO specifications, traceability/batch No., Gel time and Barcol hardness on each resin casting. |  |  |  | Barcol hardness at least 1 sample of each resin (not less than 30 of resin manufacturer’s value as per AS 1210 section 10 and/or ² EN13121-3), |
| 11 | Glass Fibre - Data sheets, PO specifications, evidence of pallet inspections and checks for water damage performed, traceability/batch No., |  |  |  | Glass fibre data sheets, evidence from MDR, photos, suppliers compliance and analysis |
| 12 | Catalysts - Data sheets, PO specifications, traceability/batch No., shelf life, expiry dates, production requirements reactive and Gel time consistency |  |  |  | Catalysts data sheets, evidence from MDR, at least 1 sample of each batch, test reports compliance certs, |
| 13 | Additives - Data sheets, PO specifications, traceability/batch No., shelf life, expiry dates, delivery, batch and pallet No. |  |  |  | Additives data sheets, evidence from MDR, batch, delivery and pallet nos. |
| 14 | Confirm major dimensions are correct per drawing |  |  |  | Attach a copy of the vessel drawing to this record sheet highlighting on the drawing which dimensions were checked. |
|  | Inlet/outlet nozzle |  |  |  |  |
| 15 | - Flange standard correct? |  |  |  | Flange face: FF / RF |
| 16 | - Class correct? |  |  |  | Class: |
| 17 | - Diameter correct? |  |  |  | Size: |
| 18 | - Pitch circle diameter correct? |  |  |  | PCD: _____________ mm |
| 19 | - Number and diameter of bolt holes correct? |  |  |  | No.:__________ Dia.:__________ mm |
| 20 | Backing Rings required? |  |  |  | Galv or 316 Stainless |
|  | Manhole |  |  |  |  |
| 21 | - Flange standard correct? |  |  |  | Flange face: FF / RF |
| 22 | - Class correct? |  |  |  | Class: |
| 23 | - Diameter correct? |  |  |  | Size: |
| 24 | - Pitch circle diameter correct? |  |  |  | PCD: _____________ mm |
| 25 | - Number and diameter of bolt holes correct? |  |  |  | No.:__________ Dia.:__________ mm |
| 26 | Other minor nozzles and tapping points per specification/drawing? |  |  |  |  |
| 27 | Backing rings required? |  |  |  | Galv or 316 Stainless |
| MANHOLE AND INTERNAL ACCESS |
| 28 | Davit for manhole cover fitted? |  |  |  | Not to be fitted to GRP/FRP vessel unless specified and rated for load |
| 29 | Internal and external grab rails fitted for manhole entry and exit? |  |  |  | Not to be fitted to GRP/FRP vessel unless specified and rated for load |
| 30 | Internal ladder complies with Australian Standards? |  |  |  | Not to be fitted to GRP/FRP vessel unless specified and rated for load |
| VESSEL THICKNESSES |
| 31 | Shell thickness correct as per drawings? |  |  |  | Shell thickness: _____________ mm |
| 32 | End thickness correct as per drawings? |  |  |  | Top head thickness: _________mm Bottom head thickness: _______ mm |
| APPURTENANCES AND INTERNALS |
| 33 | Internal grab rails, platforms and ladder(s) secure? |  |  |  | Not to be fitted to GRP/FRP vessel unless specified and rated for load |
| 34 | External access stairs to AS1657 and S151? |  |  |  |  |
| 35 | Platform structure attachment lugs fitted? |  |  |  | Not to be fitted to GRP/FRP vessel unless specified and rated for load |
| 36 | Lifting eyes correctly located and fitted? |  |  |  | If specified as per “as constructed” drawing and rated for load |
| RELIEF VALVE |
| 37 | Confirm documentation and data for relief valve is correct and as per MDR |  |  |  |  |
| 38 | Confirm relief valve serial number? |  |  |  | SN _______________ |
| 39 | Confirm relief valve has correct size and class as per specification? |  |  |  | Pressure rating = ___________ Size = __________________ |
| 40 | Confirm relief valve has been calibrated correctly (at or below design pressure of vessel and as per specification)? |  |  |  | Attach calibration certificate |
| TRANSPORT AND STORAGE |
| 41 | Nozzle cover plates and tapping point plugs installed? |  |  |  |  |

| 4. TEST | PASS | FAIL | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- |
| 42 | Confirm Material certificates are acceptable |  |  |  |  |
| 43 | Confirm pressure test results are acceptable |  |  |  |  |

Refer to AS/NZS 1210-2010 Section 10 for Design requirements of Non-Metallic Vessels.

2 Refer to BS EN13121-3 European Standard adopted by UK, for "GRP tanks and vessels for use above ground.

| 5. REMARKS / REMEDIAL / FOLLOW UP ACTIONS | ACTION BY | TARGET DATE | STATUS |
| --- | --- | --- | --- |

| 6. SIGNOFFS |
| --- |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |

POST TRANSPORTATION INSPECTION

- Inspection to be completed at point of delivery

- If a supply verification was not completed at the manufacturer, both supply verification and post transportation inspection should be completed at point of delivery.

| 7. POST TRANSPORTATION REMARKS / REMEDIAL / FOLLOW UP ACTIONS | ACTION BY | TARGET DATE |
| --- | --- | --- |

| 8. SIGNOFFS |
| --- |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |