A) INTRODUCTION

The following procedure is intended to ensure that the quality of constructed product and its associated activities are completed by competent persons and:

- Comply with current and applicable specified requirements (including Corporation specifications / contract terms and conditions, national / international standards, manufacturer’s recommendations and industry best practices.

- Are conducted in a safe and professional manner.

- Provide an audit trail for verification of Quality Assurance and Quality Control compliance.

This procedure is for use by all PUMP Competent personnel, who shall complete all inspection / construction activities and record all activities on Water Corporation Document ITP-PC-M_PUMP - Self Priming for each asset constructed.

NOTE:

- Please ensure that all ITP documents are completed by a competent person and that all Water Corporation SAFETY and operational requirements are to be complied with at all times in relation with Water Corporation and AS/NZS Standards where applicable.

B) COMPLETED DOCUMENTS

Completed documents are to be scanned and saved as a .pdf file in the relevant AQUA folder utilising the following naming convention:

LOCATION - DISCIPLINE - ASSET – ASSET TYPE – VENDOR NAME – DOCUMENT TYPE – P&ID TAG – REVISION NUMBER

E.g. RavenswoodPS_M_Valve_Butterfly_Tyco_PC_1000BV3422_1

The commissioning manager shall coordinate incorporation of completed ITPs in conjunction with the CAMEL.

Feedback on improvements to ITPs should be directed to PMB Mechanical for incorporation into future versions.

* All Pre-Commissioning documents shall contain the following sections (1 – 2) which capture generic asset information

| 1. REFERENCE INFORMATION |
| --- |
| INSPECTION DATA | ASSET DATA |
| PROJECT NAME: | MANUFACTURER: |
| LOCATION: | MF SERIAL NO: |
| INSPECTION DATE: | WC FLER / TAG NO: |
| INSPECTOR NAME: | TYPE / MODEL NO / SIZE: |
| PROJECT / CONTRACT NO: | DESIGN CRITERIA: |
| ATTENDEES: |

| 2. INSPECTION PREPARATION |
| --- |
|  | OSH compliance requirements. |
|  | Obtain QA / QC documentation (review outstanding items). |
|  | Relevant Water Corporation standards. |
|  | Relevant Australian Standards. |
|  | Supporting contract documentation / approved drawings. |
|  | Provision of required test equipment (portable vibration monitor and temperature sensor). |
|  | Provision of required test reports and certificates |
|  | Provision of completed construction verification |

| 3. INSPECTION PRELIMINARIES | YES | NO | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- |
| 1 | “Punchlist” reviewed and free of significant defects preventing asset pre-commissioning? |  |  |  |  |
| 2 | Hazard identification and risk assessment for asset pre-commissioning complete? |  |  |  |  |
| 3 | Electrical construction and pre-commissioning ITPs complete? |  |  |  |  |
| 4 | Mechanical and electrical site specific pre-requisite ITPs complete? |  |  |  |  |

*Contents of Section 4 (Inspection) and Section 5 (Test) are Asset Specific and shall reflect relevant SPS / Australian Standard(s) where practicable. Entries shall also be worded to reflect the procedures involved in a step-by-step manner; i.e. “Conduct visual inspection and ensure pre-start photographs are taken”, “Extract bearing housing covers to expose bearings and full shaft length”.

| 4. INSPECTION | YES | NO | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- |
| ROTATION |
| 1 | Pump and motor shafts rotate freely by hand without rub, noise or obvious out of balance? |  |  |  |  |
| ANCILLARY AND TEMPORARY EQUIPMENT |
| 2 | All ancillary systems available and on-line? (eg. external seal water, lube oil, cooling water, room ventilation systems) |  |  |  |  |
| 3 | Temporary instruments (if required) installed? (eg. vibration transducers, flow meters, pressure gauges) |  |  |  |  |
| CONTROL AND PROTECTION SYSTEMS |
| 4 | All electrical / instrument control and protection systems available and on-line? (eg. pump and motor protection, process control systems) |  |  |  |  |
| 5 | All mechanical / hydraulic control and protection devices available and on-line? (eg. min. flow recirculation lines, surge vessels, relief valves, bursting discs, automatic control valves) |  |  |  |  |
| HYDRAULICS |
| 6 | Pump suction water supply available |  |  |  |  |
| 7 | Pump casing primed (as per manufacturers spec)- full of liquid and all air removed? |  |  |  |  |
| 8 | All pump suction valves open? |  |  |  |  |
| 9 | Open flow path available for pumped liquid once the discharge valve is opened? |  |  |  |  |
| 10 | Seal water system primed and isolation valves open? |  |  |  |  |
| 11 | Instrument impulse lines primed and vented? |  |  |  |  |
| 12 | All connections along flow path hydraulically tight (no leaks)? |  |  |  |  |
| 13 | System static head & suction conditions suitable for pump operation? |  |  |  |  |
| 14 | Pump Grit loading rate calculated? (Refer to appendix C) |  |  |  | Grit rate: ………………….. kg/hr |
| 15 | Grit, loading chute and capture system setup and functional. |  |  |  |  |
| ACCESS |
| 16 | Area around pumpset clean, free of debris and barricaded off from other works (if required)? |  |  |  |  |
| 17 | Emergency stop pushbutton accessible? |  |  |  |  |

| 5. TEST | YES | NO | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- |
| PRESSURE TEST |
| 1 | With the isolation suction and discharge valves closed pressure test to the maximum line pressure. Check for leaks at pump nozzles, seals and tappings |  |  |  |  |
| PERFORMANCE DATA |
| 2 | “Bump” start the pump motor to ensure direction of rotation of motor is correct |  |  |  |  |
| 3 | Ambient temperature, bearing temperatures and static heads recorded prior to pump start-up? |  |  |  | Record pre-start measurements per Appendix B. |
| SELF-PRIMING PERFORMANCE ASSESSMENT |
| 4 | Pumpset self-priming performance parameters recorded during pumpset operation? |  |  |  | Record operating measurements as per Appendix B. Time to Self-Prime: ………… min/sec |
| 5 | Is priming time acceptable? |  |  |  |  |
| 6 | Bearing temperatures acceptable? |  |  |  |  |
| 7 | Bearing vibration levels acceptable? |  |  |  |  |
| 8 | Pitch and level of noise emanating from pump, motor and bearings acceptable? |  |  |  |  |
| 9 | Pump and pipework connections hydraulically tight (no leaks)? |  |  |  |  |
|  | For pumps equipped with mechanical seals: |  |  |  |  |
| 10 | - Seals are hydraulically tight (no leaks)? |  |  |  |  |
| 11 | - Seal running temperatures acceptable? |  |  |  |  |
|  | For pumps equipped with packed seals: |  |  |  |  |
| 12 | - Seal water flows within manufacturer’s recommended limits? |  |  |  |  |
| 13 | - Seal housing temperatures acceptable? |  |  |  |  |
| PUMP DUTY PERFORMANCE ASSESSMENT |
| 14 | Pumpset performance parameters recorded during operation and acceptable? |  |  |  | Record operating measurements as per Appendix B. |
| 15 | Bearing temperatures acceptable? |  |  |  |  |
| 16 | Bearing vibration levels acceptable? |  |  |  |  |
| 17 | Pitch and level of noise emanating from pump, motor and bearings acceptable? |  |  |  |  |
| 18 | Pump and pipework connections hydraulically tight (no leaks)? |  |  |  |  |
|  | For pumps equipped with mechanical seals: |  |  |  |  |
| 19 | - Seals are hydraulically tight (no leaks)? |  |  |  |  |
| 20 | - Seal running temperatures acceptable? |  |  |  |  |
|  | For pumps equipped with packed seals: |  |  |  |  |
| 21 | - Seal water flows within manufacturer’s recommended limits? |  |  |  |  |
| 22 | - Seal housing temperatures acceptable? |  |  |  |  |

| PUMP GRIT TRANSPORT PERFORMANCE ASSESSMENT |
| --- |
| 23 | Pumpset performance parameters recorded during operation and acceptable? |  |  |  | Record operating measurements as per Appendix B. |
| 24 | Bearing temperatures acceptable? |  |  |  |  |
| 25 | Bearing vibration levels acceptable? |  |  |  |  |
| 26 | Pitch and level of noise emanating from pump, motor and bearings acceptable? |  |  |  |  |
| 27 | Pump and pipework connections hydraulically tight (no leaks)? |  |  |  |  |
|  | For pumps equipped with mechanical seals: |  |  |  |  |
| 28 | - Seals are hydraulically tight (no leaks)? |  |  |  |  |
| 29 | - Seal running temperatures acceptable? |  |  |  |  |
|  | For pumps equipped with packed seals: |  |  |  |  |
| 30 | - Seal water flows within manufacturer’s recommended limits? |  |  |  |  |
| 31 | - Seal housing temperatures acceptable? |  |  |  |  |
| POST TEST CHECKS |
| 32 | Baseframe welds intact (no obvious cracking)? |  |  |  |  |
| 33 | All bolted and screwed connections tight? |  |  |  |  |

Sections 6 & 7 to be retained in all ITPs.

| 6. REMARKS / REMEDIAL / FOLLOW UP ACTIONS | ACTION BY | TARGET DATE | STATUS |
| --- | --- | --- | --- |

| 7. SIGNOFFS |
| --- |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |

APPENDIX A – SITE SPECIFIC PRE-REQUISITES

| A1. MECHANICAL PRE-REQUISITES | DONE | NO | ITR / DOCUMENT REF. |
| --- | --- | --- | --- |
|  |  |  |  | ITP-SV-M-PUMP |
|  |  |  |  | ITP-CV-M-PUMP |
| A2. ELECTRICAL PRE-REQUISITES | DONE | NO | ITR / DOCUMENT REF. |

APPENDIX B – SELF-PRIMING (GRIT) PUMP PERFORMANCE RECORD SHEET

| # | PARAMETER | UNITS | MAX. LIMIT (Note 1) | PRE START-UP | T0 (Note 2) | Prime T1 | Prime T2 | Prime T3 (DutyT0) | Duty T1 | Duty T2 | Grit T0 | Grit T1 | Grit T2 | Grit T3 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| GENERAL |  |  |  |  |  |  |
| 1 | Time (note 1) | Hrs : Min |  |  | : | +1 min | +2 min | +…….. | +5 min | +10 min | : | + 1 hr | +2 hr | +3hr |
| 2 | Ambient Temperature | °C |  |  |  |  |  |  |  |  |  |  |  |  |
| 3 | Atmospheric Pressure | Pa |  |  |  |  |  |  |  |  |  |  |  |  |
| 4 | Pipe Inside Diameters | mm |  |  |  |  |  |  |  |  |  |  |  |  |
| 5 | Suction Depth to Water (refer to appendix C) | m |  |  |  |  |  |  |  |  |  |  |  |  |
| PUMP – SELF-PRIMING, DUTY & GRIT TRANSPORT PERFORMANCE TEST |  |  |  |  |  |  |
| 6 | Grit Loading (refer App C) | Kg/hr |  |  |  |  |  |  |  |  |  |  |  |  |
| 7 | Suction Pressure / Head | kPa / m |  |  |  |  |  |  |  |  |  |  |  |  |
| 8 | Discharge Pressure / Head | kPa / m |  |  |  |  |  |  |  |  |  |  |  |  |
| 9 | Calculated Pump Head (Refer to Appendix C) | m |  |  |  |  |  |  |  |  |  |  |  |  |
| 10 | Flowrate | (l/s)(m3/hr) |  |  |  |  |  |  |  |  |  |  |  |  |
| 11 | Suction Temperature | °C |  |  |  |  |  |  |  |  |  |  |  |  |
| 12 | Discharge Temperature | °C |  |  |  |  |  |  |  |  |  |  |  |  |
| 13 | Pump - Shaft Speed | rpm |  |  |  |  |  |  |  |  |  |  |  |  |
| 14 | Grit Collection | kg |  |  |  |  |  |  |  |  |  |  |  |  |
| MOTOR |  |  |  |  |  |  |
| 15 | Power | kW |  |  |  |  |  |  |  |  |  |  |  |  |
| 16 | Voltage | V |  |  |  |  |  |  |  |  |  |  |  |  |
| 17 | Current | A |  |  |  |  |  |  |  |  |  |  |  |  |
| 18 | Frequency | Hz |  |  |  |  |  |  |  |  |  |  |  |  |
| 19 | Shaft Speed | rpm |  |  |  |  |  |  |  |  |  |  |  |  |

APPENDIX B – SELF-PRIMING (GRIT) PUMP PERFORMANCE RECORD SHEET cont’d

| # | PARAMETER | UNITS | MAX. LIMIT (Note 1) | PRE START-UP | T0 (Note 2) | Prime T1 | Prime T2 | Prime T3 (DutyT0) | Duty T1 | Duty T2 | Grit T0 | Grit T1 | Grit T2 | Grit T3 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| BEARING TEMPERATURES |  |  |  |  |  |  |
| 20 | Motor NDE | °C |  |  |  |  |  |  |  |  |  |  |  |  |
| 21 | Motor DE | °C |  |  |  |  |  |  |  |  |  |  |  |  |
| 22 | Pump DE | °C |  |  |  |  |  |  |  |  |  |  |  |  |
| 23 | Pump NDE | °C |  |  |  |  |  |  |  |  |  |  |  |  |
| BEARING VIBRATION LEVELS |  |  |  |  |  |  |
| 24 | Motor NDE (Vert.) | mm/s RMS |  |  |  |  |  |  |  |  |  |  |  |  |
| 25 | Motor NDE (Horiz.) | mm/s RMS |  |  |  |  |  |  |  |  |  |  |  |  |
| 26 | Motor NDE (Axial) | mm/s RMS |  |  |  |  |  |  |  |  |  |  |  |  |
| 27 | Motor DE (Vert.) | mm/s RMS |  |  |  |  |  |  |  |  |  |  |  |  |
| 28 | Motor DE (Horiz.) | mm/s RMS |  |  |  |  |  |  |  |  |  |  |  |  |
| 29 | Motor DE (Axial) | mm/s RMS |  |  |  |  |  |  |  |  |  |  |  |  |
| 30 | Pump DE (Vert.) | mm/s RMS |  |  |  |  |  |  |  |  |  |  |  |  |
| 31 | Pump DE (Horiz.) | mm/s RMS |  |  |  |  |  |  |  |  |  |  |  |  |
| 32 | Pump DE (Axial) | mm/s RMS |  |  |  |  |  |  |  |  |  |  |  |  |
| 33 | Pump NDE (Vert.) | mm/s RMS |  |  |  |  |  |  |  |  |  |  |  |  |
| 34 | Pump NDE (Horiz.) | mm/s RMS |  |  |  |  |  |  |  |  |  |  |  |  |
| 35 | Pump NDE (Axial) | mm/s RMS |  |  |  |  |  |  |  |  |  |  |  |  |
| NOISE LEVELS |  |  |  |  |  |  |
| 36 | Pump | dBA |  |  |  |  |  |  |  |  |  |  |  |  |
| 37 | Pipework | dBA |  |  |  |  |  |  |  |  |  |  |  |  |

Notes:  	1.	Manufacturer recommended limits (for: “Time” this refers to the specified pump suction priming time).

2.	Time T0 = the start time of the pump (once the pump has been prepared ready to test self-prime time).

APPENDIX C – EVALUATION OF TEST VALUES

- Determination of Grit Pump – Operating Grit Load (kg/hr)

Plant Grit Loading:

Calculation Option 1:

Plant Grit load: 	………….. Tonnes/wk

x 1000 / 7 =	………...... kg/day

/ 24 =	………….. kg/hr

Calculation Option 2:

(use typical Specific Grit Loading (SGL) of 4.5 kg/ML)

Design Inflow (DI): 	………….. MLD

Plant Grit load:

DI …….. (MLD) x SGL …….. (kg/ML) =	………...... kg/day

/ 24 =	………….. kg/hr

Grit Pump Duty Cycle:

(if times unknown – use typical Duty Cycle = 0.25 )

Time On: ………… min ; Time Off: ………… min

Duty Cycle = 		Time On		= ………..  (

Time On + Time Off

Grit Pump:

Operating Grit Load = 	Plant Grit Load (kg/hr)	= ………….. kg/hr

Duty Cycle

- Suction – Depth to Water (DTW) (Pump Lift):

Tank Water Level (WL): 	Min RL	……… m

Max RL	……… m

Pump Suction (PS) RL	……… m

DTW (max) = PS ……………. – WL (min) ……………. = ……………. m

DTW (min) = PS ……………. – WL (max) ……………. = ……………. m

- Flow Rate Q

The measured values from magnetic flowmeter (m3/hour)

- Total Head H

pb [Pa] Atmospheric pressure

pd [Pa] Static pressure on discharge side, related to shaft centreline of pump

ps [Pa] Static pressure at suction side, related to shaft centreline of pump

zd, zs [m] Height difference between measurement device and shaft centreline on suction and discharge side

HY [m] Height difference between the reference planes of suction and discharge side (geodetic head)

HV [m] Head losses, the sum of all suction and discharge losses

vs [m/s] Velocity in the suction pipe at the measuring point =  Q/As

vd [m/s] Velocity in the discharge pipe at the measuring point = Q/Ad

ρs [kg/m³] Density of fluid (water) on suction side at Ts and ps taken from VDI Table of Steam Properties

ρd [kg/m³] Density of fluid (water) on discharge side at Td and pd taken from VDI Table of Steam Properties

g [m/s²] Gravitational constant

- Pump Efficiency

Q [m³/h] Flow rate

H [m] Total head

ρm [kg/m³] Average density of fluid (water) taken from VDI Table of Steam Properties

g [m/s²] Gravitational constant

Pp [kW] Pump input power