| All ITR documents to be completed & witnessed by competent person/s Compliance to be achieved to contract requirements and all latest versions of applicable standards |
| --- |
| 1. REFERENCE INFORMATION |
| INSPECTION DATA | ASSET DATA |
| PROJECT NAME: | MANUFACTURER: |
| LOCATION: | MF SERIAL NO: |
| INSPECTION DATE: | WC FLER / TAG NO: |
| INSPECTOR NAME: | TYPE / MODEL NO / SIZE: |
| PROJECT / CONTRACT NO: | DESIGN CRITERIA: |
| ATTENDEES: |

| 2. INSPECTION PREPARATION |
| --- |
|  | OSH compliance requirements. |
|  | Obtain QA / QC documentation (review outstanding items). |
|  | Relevant Water Corporation standards |
|  | Relevant Australian Standards. |
|  | Supporting contract documentation / approved drawings. - Drawings for Cabinet / HPU, Valve GA, Hydraulic cylinder and Hydraulic circuit. Hydraulic Specification and Contract Documentation |
|  | Provision of required test equipment. |
|  | Provision of required test reports and certificates; i.e. hydrostatic test, material certificates, etc. |

| 3. PUMP EQUIPMENT DATA |  |
| --- | --- |
| EQUIPMENT TYPE: |  |
| MODEL: |  |
| SERIAL NO.: |  |
| MANUFACTURER: |  |
| RATED FLOW RATE: | (cc/rev x RPM / 1000 = l/sec) |
| POWER SUPPLY: |  |
| ADDITIONAL INFORMATION: |  |

| 4. PLC DATA |  |
| --- | --- |
| EQUIPMENT TYPE: |  |
| MODEL: |  |
| SERIAL NO.: |  |
| MANUFACTURER: |  |
| ADDITIONAL INFORMATION: |  |

| 5. INSPECTION | YES | NO | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- |
| Hydraulics Cabinet |
| 1 | Cabinet dimensions correct? |  |  |  |  |
| 2 | Cabinet material? | Marine Aluminium or 316 Stainless Steel |
| 3 | Confirm IP56 or greater |  |  |  |  |
| 4 | Bund Capacity 110% of fluid stored within Cabinet |  |  |  |  |
| 5 | Operation of doors and door restraints |  |  |  |  |
| 6 | Doors fitted with lockable Hasp and Staple handle to fit WC padlock or L shape to accommodate Bilock cylinder |  |  |  |  |
| 7 | Door switches fitted |  |  |  |  |
| 8 | Cabinet lighting adequate |  |  |  |  |
| 9 | Cabinet design to accommodate bottom entry of cables |  |  |  |  |
| 10 | Access to equipment satisfactory? |  |  |  |  |
| 11 | Base plate correct? Anchor Holes ≥16mm |  |  |  |  |
| 12 | Lifting points as per drawing? |  |  |  |  |
| 13 | Instruction Panel / Hydraulic Circuit available |  |  |  |  |
| 14 | Identification name plate affixed? |  |  |  |  |
| 15 | Corrosion mitigation acceptable? Insertion rubber used between dissimilar metals? |  |  |  |  |
| 16 | Hydraulic pipework entry/exit |  |  |  | (LHS/RHS/Bottom) |
| 17 | Cable entry/exit |  |  |  | (LHS/RHS/Bottom) |
| 18 | Pipework Supports |  |  |  |  |
| 19 | All internal and external fasteners correct? |  |  |  |  |
| 20 | General Quality and Workmanship |  |  |  |  |
| 21 | Anti-Condensate Heaters fitted? |  |  |  | Temp. Setting - |
| 22 | Total Weight |  |  |  | kgs |
| Hydraulics Power Unit |
| 1 | Hydraulic system as per Hydraulic Circuit Drawing |  |  |  |  |
| 2 | Duty / Standby Hydraulic Pumps |  |  |  |  |
| 3 | Emergency Hand Pump fitted |  |  |  |  |
| 4 | Reservoir fully sealed? Can top cover be removed for access and cleaning? |  |  |  |  |
| 5 | Reservoir Air Desiccant Breather fitted? |  |  |  |  |
| 6 | Reservoir Size – Check volume is 150% system capacity |  |  |  | Litres |
| 7 | Filler pipe has easy access, over bund area with filter |  |  |  |  |
| 8 | Low hydraulic oil switch fitted? |  |  |  |  |
| 9 | Temperature Gauge / indicator fitted? |  |  |  |  |
| 10 | Pump suction location acceptable? |  |  |  |  |
| 11 | Reservoir drain height above floor acceptable? |  |  |  |  |
| 12 | Reservoir floor sloped to drain point? |  |  |  |  |
| 13 | Drain line fitted with stop valve and plug? |  |  |  |  |
| 14 | Hydraulic System Pressure Filter |  |  |  | Micron |
| 15 | Hydraulic System Return Line Filter |  |  |  | Micron |
| 16 | Hydraulic manifolds clearly labelled? |  |  |  |  |
| 17 | Fluid Level Indicator Min & Max oil level clearly labelled? |  |  |  |  |
| 18 | Pressure Gauge Fitted |  |  |  | Range - |
| 19 | Recommended Hydraulic fluid |  |
| 20 | Relief valve fitted on all pump delivery lines? |  |  |  |  |
| 21 | Maximum Pump Delivery Pressure? |  |  |  | Bar / PSI |
| 22 | All solenoid valves 24 VDC? |  |  |  |  |
| 23 | Solenoid valve mechanical overrides present and working? |  |  |  |  |
| 24 | Magnetic Drain Plug fitted |  |  |  |  |
| Hydraulics Control Panel & PLC Functional Control |
| 1 | Lockable On / Off Selector Switch for each valve |  |  |  |  |
| 2 | Open, Close and Stop button for each valve |  |  |  |  |
| 3 | Local indication for Valve Fully open, Valve Fully Closed, High Oil Temp, Low Oil Level, Hydraulic Pump Fault |  |  |  |  |
| 4 | Labelling correct? |  |  |  |  |
| 5 | Pump fault generated if valve comes off proximity switch 3 times or more in 1 hour? |  |  |  |  |
| 6 | Proximity switches => 5A at 30VDC or 2A at 250 VAC |  |  |  |  |
| 7 | Valve alarm generated in event of power failure |  |  |  |  |
| 8 | Electrical Switchboard conforms to WC DS26-09 |  |  |  |  |
| 9 | Electrical switchboard accommodates Bilock cylinder barrel for access behind switchboard panel |  |  |  |  |

| 6. OPERATIONAL TESTING | YES | NO | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- |
| 1 | Check system for leaks |  |  |  |  |
| 2 | Pump Rotation correct and labelled? |  |  |  |  |
| 3 | Check bearings, motors and pumps for excessive vibration |  |  |  |  |
| 4 | Monitor hydraulic fluid temperature |  |  |  | Temp. switch setting: degrees |
| 5 | Minimum 10 starts in 1hr period |  |  |  |  |
| 6 | All 24v solenoid valves operate correctly? |  |  |  |  |
| 7 | High Pressure switch operates correctly |  |  |  |  |
| 8 | Flow switch operates correctly |  |  |  | Range? |
| 9 | Confirm operation of flow control valves |  |  |  |  |
| 10 | Confirm operation of isolation valves |  |  |  |  |
| 11 | Confirm Operation of Hand Pump |  |  |  |  |
| 12 | Confirm Operation of Flow sensing switch |  |  |  |  |
| 13 | Record relief valve pressure (Pump 1 & 2) | Bar / PSI |
| 14 | Record relief valve pressure (Hand pump) | Bar / PSI |
| 15 | Record pressure switch setting | Bar / PSI |
| 16 | Record cylinder stroke and stroke time | mm secs |
| 17 | Record pump flow |  |
| 18 | Confirm motor interlock on high oil temp |  |
| 19 | Confirm motor interlock on low oil level |  |
| 20 | Confirm pressure and return filter block generates fault but allows pump to run |  |
| 21 | Confirm lamp test |  |
| 22 | Record results in Manufacturer’s ITP’s |  |  |  |  |

Note:      System to be drained prior to transporting to WA

7. REMARKS / REMEDIAL ACTIONS

Manufacturer’s recommended hydraulic piping material, gauge and size -

| 8. SIGNOFFS |  |
| --- | --- |
| NAME (PRINT) | COMPANY / ROLE (Water Corporation) | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE (Manufacturer) | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE (Valve Supplier) | SIGNATURE | DATE |

# Comments

Footer data copied from non related document – please check and update footer information particular to this document