- All ITR documents to be completed & witnessed by competent person/s

- Compliance to be achieved to contract requirements and all latest versions of applicable standards

| 1. REFERENCE INFORMATION |
| --- |
| INSPECTION DATA | ASSET DATA |
| PROJECT NAME: | MANUFACTURER: |
| LOCATION: | MF SERIAL NO: |
| INSPECTION DATE: | WC FLER / TAG NO: |
| INSPECTOR NAME: | TYPE / MODEL NO / SIZE: |
| PROJECT / CONTRACT NO: | DESIGN CRITERIA: |
| ATTENDEES: |

| 2. INSPECTION PREPARATION |
| --- |
|  | OSH compliance requirements. |
|  | Obtain QA / QC documentation (review outstanding items). |
|  | Relevant Water Corporation standards. |
|  | Relevant Australian Standards. |
|  | Supporting contract documentation / approved drawings. |
|  | Provision of required test equipment. |
|  | Provision of required test reports and certificates; i.e. hydrostatic test, material certificates, etc. |

| 3. INSPECTION | YES | NO | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- |
| GENERAL |
| 1 | Visually inspect valve installation and verify correct installation as per manufacturer’s recommendations |  |  |  |  |
| 2 | Confirm that valve location is correct as per drawings |  |  |  |  |
| 3 | Verify correct orientation / direction of flow for installed valve |  |  |  |  |
| 4 | Valve support adequate? |  |  |  |  |
| 5 | Adjacent pipework supported independently of valve? |  |  |  |  |
| 6 | Local upstream and downstream isolation available for valve? |  |  |  |  |
| 7 | Inspection / access covers clear of obstructions per drawings? |  |  |  |  |
| 8 | Confirm test points and relief valve outlet (for RPZ devices) is accessible and free of obstruction |  |  |  |  |
| 9 | Confirm The RPZ complies with AS3500 requirement i.e. that it is installed with a minimum of 300mm clearance above ground |  |  |  | 300mm from under side of relief drain of RPZ valve To be installed external to dosing panels i.e. not to be in an enclosure to allow ease of testing and leak detection To be installed in a cage in wastewater applications To be tested and certified by competent Plumber with RPZD accreditation/training Dated stainless steel tag to be placed on RPZ on completion of in-situ certification by Plumber When installed in a chemical dosing module a tundish to be placed under relief drain to direct discharge safely away thus preventing pooling at the same time |
| BOLT-UP |
| 10 | Check that mating flanges are flat, clean and free of irregularities |  |  |  |  |
| 11 | Verify gasket material and thickness |  |  |  | Material: CMF EPDM Other _____________________ Thickness: _________________mm |
| 12 | Confirm all bolts installed on valve and that bolt sizes, material and grade are correct |  |  |  | Size: ________ Material: __________ Grade: 4.6 8.8 Other: _______ |
| 13 | Confirm that associated nut grade is correct |  |  |  | Grade: 5 8 Other __________ |
| 14 | Check that valve disc is in correct position during bolt-up and tightening |  |  |  |  |
| 15 | Confirm correct protrusion of bolt threads past nut |  |  |  | Protrusion: _____________________ |
| 16 | Confirm correct bolt tightening sequence has been followed |  |  |  |  |
| 17 | Verify bolt torque requirements comply with DS-38. Also verify actual bolt torque applied to each bolt is correct |  |  |  | DS38 bolt torque: _____________Nm Actual bolt torque: _____________Nm |
| 18 | Verify that torque wrench / machine used is calibrated |  |  |  | Calibration certificate date: _________ |
| 19 | If required by design, verify that flange isolation materials have been installed correctly |  |  |  |  |
| 20 | Check that earth ring(s) have been installed correctly |  |  |  |  |
| 21 | Verify that bonding link(s) have been installed correctly |  |  |  |  |
| ISOLATING JOINTS (IF REQUIRED FOR DISSIMILAR METALS OR CATHODIC PROTECTION ISOLATION) |
| 22 | Check that correct isolating bolt sleeves and washers have been installed |  |  |  |  |
| 23 | Verify that flange to flange isolation is acceptable |  |  |  |  |
| 24 | Verify that a test post has been installed |  |  |  |  |
| 25 | Confirm if a surge diverter has been installed |  |  |  |  |

| 4. TEST | YES | NO | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- |
| 1 | Open / close operation satisfactory if possible? |  |  |  |  |
| 2 | Final position of valve correct? |  |  |  | Open Closed |

| 5. COATINGS INSPECTION | YES | NO | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- |
| 1 | Check that valve external coating is free of damage |  |  |  |  |
| 2 | Confirm that valve wrapping is satisfactory (buried service only) |  |  |  |  |

| 6. REMARKS / REMEDIAL / FOLLOW UP ACTIONS | ACTION BY | TARGET DATE | STATUS |
| --- | --- | --- | --- |

| 7. SIGNOFFS |
| --- |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |