- All ITR documents to be completed & witnessed by competent person/s

- Compliance to be achieved to contract requirements and all latest versions of applicable standards

| 1. REFERENCE INFORMATION |
| --- |
| INSPECTION DATA | ASSET DATA |
| PROJECT NAME: | MANUFACTURER: |
| LOCATION: | MF SERIAL NO: |
| INSPECTION DATE: | WC FLER / TAG NO: |
| INSPECTOR NAME: | TYPE / MODEL NO / SIZE: |
| PROJECT / CONTRACT NO: | DESIGN CRITERIA: |
| ATTENDEES: |

| 2. INSPECTION PREPARATION |
| --- |
|  | OSH compliance requirements. |
|  | Obtain QA / QC documentation (review outstanding items). |
|  | Relevant Water Corporation standards. |
|  | Relevant Australian Standards. |
|  | Supporting contract documentation / approved drawings. |
|  | Provision of required test equipment. |
|  | Provision of required test reports and certificates; i.e. hydrostatic test, material certificates, etc. |

| 3. INSPECTION | YES | NO | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- |
| GENERAL |
| 1 | Locate and verify that name plate details match valve specification |  |  |  |  |
| 2 | Direction of flow clearly visible on nameplate or valve body? |  |  |  |  |
| 3 | Weight of valve clearly indicated? |  |  |  | Kg: |
| 4 | Critical spares for valve supplied? |  |  |  |  |
| 5 | Inspect valve to ensure equipment is adequately clean |  |  |  |  |
| 6 | Confirm if O&M Manuals have been provided (hardcopy / softcopy) |  |  |  | Hardcopy / softcopy? (please circle) |
| MATERIALS AND ARRANGEMENT |
| 7 | Verify construction materials (refer to valve name plate) with specification and relevant drawings |  |  |  |  |
| 8 | Confirm pattern design (oblique, angled or globe) meets specification and relevant drawings |  |  |  |  |
| 9 | Measure face to face length of valve and verify correct length with manufacturer dimensions or general arrangement drawing(s). |  |  |  | Length: Checked against: MF Dimensions / G.A. Dwg |
| 10 | Confirm flange details on name plate match specifications |  |  |  | Flange Aust. Standard/ISO/ANSI/JIS: Flange Type: Flange Size: Flange Class: |
| 11 | Measure pitch circle diameter of valve and verify with specification / relevant Standards |  |  |  | PCD: |
| 12 | Count number of bolt holes and measure bolt hole diameters. Verify number and diameter lengths with specification / relevant Standards |  |  |  | No.: Dia: |
| 13 | Confirm lifting lugs supplied and installed |  |  |  |  |
| 14 | Confirm test taps (cover, upstream and downstream) supplied and installed |  |  |  |  |
| 15 | Confirm upstream spring is installed and secure |  |  |  | Note downstream spring is not visible as it is located in the reduced pressure zone. |
| 16 | Confirm integral relief valve is securely fastened to valve body for RPZ devices |  |  |  |  |
| 16 | Confirm relief valve port is free of debris |  |  |  | Note the relief seal holder is often visible from relief port |

| 4. TEST | PASS | FAIL | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- |
|  | Test certificates received and acceptable: |  |  |  | Attach certificates to this record |
| 1 | - Body hydrostatic test? |  |  |  |  |
| 2 | - Seat hydrostatic test? |  |  |  |  |
| 3 | - Coating continuity test? |  |  |  |  |

| 5. REMARKS / REMEDIAL / FOLLOW UP ACTIONS | ACTION BY | TARGET DATE | STATUS |
| --- | --- | --- | --- |

| 6. MECHANICAL SIGNOFFS |
| --- |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |

| 7. COATINGS INSPECTION | YES | NO | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- |
| 1 | Verify coating system and specification ensuring that product is approved for purpose. Confirm internal coating is potable water approved. |  |  |  |  |
| 2 | Consider if ambient conditions are acceptable for holiday testing. Surface temperature should be least 3ºC above dew point and relative humidity less than 85 % before testing. Surface dry and clean for holiday testing. |  |  |  |  |
| 3 | Check internal coating type and verify in accordance with relevant specification (circle D1: Epoxy Coating on Steel/Cast Iron or state, A1: Surface Preparation. |  |  |  | A1/ D1 / OTHER _____________ |
| 4 | Conduct ²dry film thickness (DFT) measurements in at least 10 locations and record values in tables below. |  |  |  |  |
| 5 | Visually inspect condition of internal and external coating appearance including uniformity, colour and free from runs, sags, and inclusions. |  |  |  |  |
| 6 | Carry out spark test on internal coating in accordance to AS/NZS 3894.1 Continuity testing of non-conductive coating – High Voltage (brush) method. Specify voltage at which test is carried out. |  |  |  | Test Voltage: V Pass Fail |
| 7 | Carry out spark test on external coating accordance to AS/NZS 3894.1 Continuity testing of non-conductive coating – High Voltage (brush) method. Specify voltage at which test is carried out. |  |  |  | Test Voltage: V Pass Fail |
| 8 | Valve passes coating condition assessment in accordance with a forementioned tests and inspection. |  |  |  |  |

Refer to AS/NZS 1627 series for Metal Finishing – Preparation and Pre-treatment of Surfaces

2 Refer to AS/NZS 3894.3 methods for Determination of Dry Film Thickness

| 7a. INTERNAL INSPECTION (Microns - DFT) |
| --- |
| NUMBER OF READS (10) | HIGH | LOW | AVERAGE |
| Comments |  |

| 7b. EXTERNAL INSPECTION (Microns - DFT) |
| --- |
| NUMBER OF READS (10) | HIGH | LOW | AVERAGE |
| Comments |  |

| 7c. FLANGE INSPECTION (Microns - DFT) |
| --- |
| NUMBER OF READS (10) | HIGH | LOW | AVERAGE |
| Comments |  |

| 7d. REMARKS / REMEDIAL / FOLLOW UP ACTIONS | ACTION BY | TARGET DATE | STATUS |
| --- | --- | --- | --- |

| 7e. COATING SIGNOFFS |
| --- |
| SUPPLIER NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |

POST TRANSPORTATION INSPECTION

- Inspection to be completed at point of delivery

- If a supply verification was not completed at the manufacturer, both supply verification and post transportation inspection should be completed at point of delivery.

| 8. POST TRANSPORTATION REMARKS / REMEDIAL / FOLLOW UP ACTIONS | ACTION BY | TARGET DATE |
| --- | --- | --- |

| 9. DELIVERY SIGNOFFS |
| --- |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |