| All ITR documents to be completed & witnessed by competent person/s Compliance to be achieved to contract requirements and all latest versions of applicable standards |
| --- |
| 1. REFERENCE INFORMATION |
| INSPECTION DATA | ASSET DATA |
| PROJECT NAME: | MANUFACTURER: |
| LOCATION: | MF SERIAL NO: |
| INSPECTION DATE: | WC FLER / TAG NO: |
| INSPECTOR NAME: | TYPE / MODEL NO / SIZE: |
| PROJECT / CONTRACT NO: | DESIGN CRITERIA: |
| ATTENDEES: |

| 2. INSPECTION PREPARATION |
| --- |
|  | OSH compliance requirements. |
|  | Obtain QA / QC documentation (review outstanding items). |
|  | Relevant Water Corporation standards. |
|  | Relevant Australian Standards. |
|  | Supporting contract documentation / approved drawings. |
|  | Provision of required test equipment. |
|  | Provision of required test reports and certificates; i.e. hydrostatic test, material certificates, etc. |

| 3. INSPECTION | YES | NO | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- |
| GENERAL |
| 1 | Visually inspect valve installation and verify correct installation as per manufacturer’s recommendations |  |  |  |  |
| 2 | Confirm that valve location is correct as per drawings |  |  |  |  |
| 3 | Confirm inlet pipework inclusive of isolation valves are of the correct size such that they do not impede surge relief |  |  |  |  |
| 4 | Check that the valve is accessible and at correct height above floor |  |  |  | Height of valve: _________mm |
| 5 | Check that mating flanges are flat, clean and free of irregularities prior to bolting -up |  |  |  |  |
| 6 | Verify gasket material and thickness |  |  |  | Material: Thickness: |
| 7 | Confirm all bolts are installed on valve and that bolt sizes, material and grade are correct |  |  |  | Size: ________ Material: __________ Grade: 4.6 8.8 Other: _______ |
| 8 | Confirm that associated nut grade is correct |  |  |  | Grade: 5 8 Other __________ |
| 9 | Confirm correct protrusion of bolt threads past nut |  |  |  | Protrusion: _____________________ |
| 10 | Confirm correct bolt tightening sequence has been followed |  |  |  |  |
| 11 | Verify bolt torque requirements comply with DS-38 unless manufacturers recommendation are less. Also verify actual bolt torque applied to each bolt is correct |  |  |  | DS38 bolt torque: _____________Nm Actual bolt torque: _____________Nm |
| 12 | Verify that torque wrench / machine used is calibrated |  |  |  | Calibration certificate date: _________ |
| 13 | Confirm that bore area of connection from pipework is at least as large as valve inlet |  |  |  | Any undue restrictions on the inlet side may affect the surge relief |
| 14 | Confirm that no other connections allowing flow exist between the pipework and surge relief valve inlet |  |  |  |  |
| 15 | Confirm that surge relief valve is positioned such that any discharge is made in a safe location |  |  |  |  |
| 16 | Confirm that the bore of any discharge pipes is at least as large as the outlet of the relief valve |  |  |  |  |
| 17 | Confirm that discharge pipes are arranged as to facilitate drainage |  |  |  |  |
| 18 | Confirm whether silencers are fitted to discharge pipe work |  |  |  |  |
| 19 | Confirm that surge relief isolation valves are locked open and/or protected from interference |  |  |  | If the relief valve is installed on a vessel, there shall be no isolation valves between the vessel and the relief valve |
| 20 | Confirm that relief valve is easily accessible for maintenance, inspection and removal |  |  |  |  |
| 4. TEST |
| 1 | Confirm manual operation lever on the isolation is operable without being too loose |  |  |  |  |
| 2 | If a site pressure test with water is practical, pressurise the pipework to the relief setting and confirm the opening of the valve. |  |  |  | Often the valve will have a test port on the body of the valve. If testing of the entire pipework is not practical, use the test port to confirm relief setting |

| 5. COATINGS INSPECTION | YES | NO | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- |
| 1 | Check that valve external coating is free of damage |  |  |  |  |

| 6. REMARKS / REMEDIAL / FOLLOW UP ACTIONS | ACTION BY | TARGET DATE | STATUS |
| --- | --- | --- | --- |

| 7. SIGNOFFS |
| --- |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |