A) INTRODUCTION

The following procedure is intended to ensure that the quality of constructed product and its associated activities are completed by competent persons and:

- Comply with current and applicable specified requirements (including Corporation specifications / contract terms and conditions, national / international standards, manufacturer’s recommendations and industry best practices.

- Are conducted in a safe and professional manner.

- Provide an audit trail for verification of Quality Assurance and Quality Control compliance.

This procedure is for all REGULATING VALVE SLEEVE. Competent personnel shall complete all inspection / construction activities and record all activities on Water Corporation Document ITP-CV-M-VALVE-REGULATING-SLEEVE for each asset constructed.

NOTE:

- Please ensure that all ITP documents are completed by a competent person and that all Water Corporation SAFETY and operational requirements are to be complied with at all times in relation with Water Corporation and AS/NZS Standards where applicable.

B) COMPLETED DOCUMENTS

Completed documents are to be scanned and saved as a .pdf file in the relevant AQUA folder utilising the following naming convention:

LOCATION - DISCIPLINE - ASSET – ASSET TYPE – VENDOR NAME – DOCUMENT TYPE – P&ID TAG – REVISION NUMBER

E.g. RavenswoodPS_M_Valve_Butterfly_Tyco_CV_1000BV3422_1

The commissioning manager shall coordinate incorporation of completed ITPs in conjunction with the CAMEL.

Feedback on improvements to ITPs should be directed to MESB Mechanical for incorporation into future versions.

| 1. REFERENCE INFORMATION |
| --- |
| INSPECTION DATA | ASSET DATA |
| PROJECT NAME: | MANUFACTURER: |
| LOCATION: | MF SERIAL NO: |
| INSPECTION DATE: | WC FLER / TAG NO: |
| INSPECTOR NAME: | TYPE / MODEL NO / SIZE: |
| PROJECT / CONTRACT NO: | DESIGN CRITERIA: |
| ATTENDEES: |

| 2. INSPECTION PREPARATION |
| --- |
|  | OSH compliance requirements. |
|  | Obtain QA / QC documentation (review outstanding items). |
|  | Relevant Water Corporation standards. |
|  | Relevant Australian Standards. |
|  | Supporting contract documentation / approved drawings. |
|  | Provision of required test equipment. |
|  | Provision of required test reports and certificates; i.e. hydrostatic test, material certificates, etc. |

| 3. INSPECTION | YES | NO | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- |
| GENERAL |
| 1 | Visually inspect valve installation and verify correct installation as per manufacturer’s recommendations |  |  |  |  |
| 2 | Confirm that valve location is correct as per drawings |  |  |  |  |
| 3 | Verify correct orientation / direction of flow for installed valve |  |  |  |  |
| 4 | Number of straight pipe diameters provided upstream and downstream of valve correct? |  |  |  |  |
| 5 | Valve support adequate? |  |  |  |  |
| 6 | Adjacent pipework supported independently of valve? |  |  |  |  |
| 7 | Local upstream and downstream isolation available for valve? |  |  |  |  |
| 8 | Inspection / access covers clear of obstructions per drawings? |  |  |  |  |
| BOLT-UP |
| 9 | Check that mating flanges are flat, clean and free of irregularities |  |  |  |  |
| 10 | Verify gasket material and thickness |  |  |  | Material: CMF EPDM Other _____________________ Thickness: _________________mm |
| 11 | Confirm all bolts installed on valve and that bolt sizes, material and grade are correct |  |  |  | Size: ________ Material: __________ Grade: 4.6 8.8 Other: _______ |
| 8 | Confirm that associated nut grade is correct |  |  |  | Grade: 5 8 Other __________ |
| 9 | Check that valve disc is in correct position during bolt-up and tightening |  |  |  |  |
| 10 | Confirm correct protrusion of bolt threads past nut |  |  |  | Protrusion: _____________________ |
| 11 | Confirm correct bolt tightening sequence has been followed |  |  |  |  |
| 12 | Verify bolt torque requirements comply with DS-38. Also verify actual bolt torque applied to each bolt is correct |  |  |  | DS38 bolt torque: _____________Nm Actual bolt torque: _____________Nm |
| 13 | Verify that torque wrench / machine used is calibrated |  |  |  | Calibration certificate date: _________ |
| 14 | If required by design, verify that flange isolation materials have been installed correctly |  |  |  |  |
| 15 | Check that earth ring(s) have been installed correctly |  |  |  |  |
| 16 | Verify that bonding link(s) have been installed correctly |  |  |  |  |
| ISOLATING JOINTS (IF REQUIRED FOR DISSIMILAR METALS OR CATHODIC PROTECTION ISOLATION) |
| 17 | Check that correct isolating bolt sleeves and washers have been installed |  |  |  |  |
| 18 | Verify that flange to flange isolation is acceptable |  |  |  |  |
| 19 | Verify that a test post has been installed |  |  |  |  |
| 20 | Confirm if a surge diverter has been installed |  |  |  |  |

| 4. TEST | YES | NO | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- |
| MANUAL OPERATION - APPLIES TO MANUAL VALVES AND MANUAL OVERIDE OF ELECTRICALLY ACTUATED VALVES |
| 1 | Confirm that the valve starting position is closed. Close the valve if not already so |  |  |  |  |
| 2 | Slowly open the valve to fully open and confirm smooth valve operation during opening and that the required force to open the valve is not excessive |  |  |  |  |
| 3 | Confirm that the valve open position indication is correct when in the fully open position |  |  |  |  |
| 4 | Slowly close the valve to fully closed and confirm smooth valve operation during closure and that the required force to close the valve is not excessive |  |  |  |  |
| 5 | Verify the direction of rotation to close |  |  |  | Direction of rotation to close: Anti-clockwise Clockwise |
| 6 | Count the number of turns between fully open and fully closed |  |  |  | Number of turns: ________________ |
| 7 | Confirm that the valve closed position indication is correct when in the fully closed position |  |  |  |  |
| ELECTRIC ACTUATOR (TO BE COMPLETED WITH COMPETENT ELECTRICAL PERSONNEL) |
| 8 | Confirm that the actuator is set up for correct direction of rotation to open and close the valve |  |  |  |  |
| 9 | Verify that open and close travel limits have been set up and that selected travel limit types (position or torque) are suitable for the valve type, with travel limit settings set correctly |  |  |  | Travel limit type: Position Torque |
| 10 | Confirm that the maximum opening and closing torque limits have been set up correctly ensuring that torque limits do not exceed the maximum rated input torque for the valve gearbox |  |  |  | Gearbox maximum rated input torque: _______________Nm |
| 11 | Confirm that actuator position (% open) is correct during operation |  |  |  |  |
| 12 | Verify that the actuator operates with uniform speed between 0% - 100% open |  |  |  |  |
| 13 | Check that travel limit switches operate correctly |  |  |  |  |
| 14 | Confirm that opening and closing running torques, breakout torques and seating torques are not excessive and the valve operates smoothly |  |  |  |  |
| 15 | Verify opening and closing times are correct for valve type and size |  |  |  | Opening / closing times: ___________ |

| 5. COATINGS INSPECTION | YES | NO | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- |
| 1 | Check that valve internal coating is free of damage |  |  |  |  |
| 2 | Check that valve external coating is free of damage |  |  |  |  |

| 6. REMARKS / REMEDIAL / FOLLOW UP ACTIONS | ACTION BY | TARGET DATE | STATUS |
| --- | --- | --- | --- |

| 7. SIGNOFFS |
| --- |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |